## Tray
Excel Cable
Containment Sizing - Tray
Notes: | This spreadsheet is for guidance only.
This may be used for Tray only - continuous flat surface
The maximum stack height of cables on a continuous surface is 150mm.
Refer "Basket" tab of spreadsheet for non-continuous containment
Tray Dimensions |  |  |  | Number of Cables
|  |  |  | 100-912 Cat 7A Plus S/FTP (1200 MHz) (Dca) | 100-910 Cat 7A S/FTP (1000 MHz) (Dca) | 190-910 Cat 7A S/FTP (1000 MHz) (B2ca) | 100-189 Cat 6A U/UTP (Dca) | 170-196 Cat 6 A F/FTP "S" Foil (Dca) | 170-196 Cat 6 A F/FTP "S" Foil (Cca) | 170-191 Cat 6 A U/FTP "S" Foil (Dca) | 170-191 Cat 6 A U/FTP "S" Foil (Cca) | 190-914 Cat 6A S/FTP (B2ca) | 190-071-500 Cat 6 U/UTP (B2ca) | 100-071 Cat 6 U/UTP (Dca) | 100-076 Cat 6 F/UTP (Dca) | 100-080 Cat6 RD U/UTP (Dca) | 100-609 Residential Category 6 U/UTP | 100-066 Cat 5e U/UTP | 100-217 Cat 5e F/UTP
Width | 600 | mm
Height | 75 | mm | Diameter of Cable | 8.5 | 7.8 | 7.8 | 8.3 | 6.9 | 6.9 | 6.7 | 6.7 | 7.5 | 6.5 | 6.2 | 7.2 | 5.4 | 4.6 | 5.2 | 6.4
Spare Capacity | 25 | % | Area of Cable | 56.745 | 47.7836 | 47.7836 | 54.1061 | 37.3928 | 37.3928 | 35.2565 | 35.2565 | 44.1786 | 33.1831 | 30.1907 | 40.715 | 22.9022 | 16.619 | 21.2372 | 32.1699
Area of Containment | 45000 | mm² | Number of Cables | 317 | 377 | 377 | 333 | 481 | 481 | 511 | 511 | 407 | 542 | 596 | 442 | 786 | 1083 | 848 | 560
Usable area | 36000 | mm²
Only edit blue cells
| This spreadsheet is for information only. Based on EN 50174-2:2018 | [13 empty] | Rev 6: October 2018
NOTE: Accurate at time of publication, higher Euroclass levels of unscreened cables are typically slightly larger in OD so please check Specification Sheets.

## Basket
Excel Cable
Containment Sizing - Basket or Ladder
Notes: | This spreadsheet is for guidance only.
This may be used for Basket or Ladder - non-continuous surface
The maximum stack height of cables on a continuous surface is 150mm. This is reduced to 125mm for basket/ladder spacing greater than 100mm
Basket / Ladder Dimensions |  |  |  | Number of Cables
|  |  |  | 100-912 Cat 7A Plus S/FTP (1200 MHz) | 100-910 Cat 7A S/FTP (1000 MHz) | 100-189 Cat 6A U/UTP | 100-196 Cat 6 A F/FTP "S" Foil | 100-191 Cat 6 A U/FTP "S" Foil | 100-914 Cat 6A S/FTP | 190-071-500 Cat 6 U/UTP (B2ca) | 100-071 Cat 6 U/UTP | 100-076 Cat 6 F/UTP | 100-080 Cat6 RD U/UTP | 100-609 Residential Category 6 U/UTP | 100-066 Cat 5e U/UTP | 100-217 Cat 5e F/UTP
Distance between supports | 100 | mm
Width | 600 | mm
Height | 50 | mm | Diameter of Cable | 8.5 | 7.8 | 8.3 | 6.9 | 6.7 | 7.5 | 6.5 | 6.2 | 7.6 | 5.4 | 4.6 | 5.2 | 6.4
Spare Capacity | 25 | % | Area of Cable | 56.745 | 47.7836 | 54.1061 | 37.3928 | 35.2565 | 44.1786 | 33.1831 | 30.1907 | 45.3646 | 22.9022 | 16.619 | 21.2372 | 32.1699
Area of Containment | 30000 | mm² | Number of Cables | 211 | 251 | 222 | 321 | 340 | 272 | 362 | 397 | 265 | 524 | 722 | 565 | 373
Usable area | 24000 | mm²
Maximum Cable Stack Height | 125 | mm
Only edit blue cells
| This spreadsheet is for information only. Based on EN 50174-2:2018 | [10 empty] | Rev 6: October 2018
NOTE: Accurate at time of publication, higher Euroclass levels of unscreened cables are typically slightly larger in OD so please check Specification Sheets.

## Conduit
Excel Cable
Containment Sizing - Conduit
Notes: | This spreadsheet is for guidance only.
This may be used for Conduit
It assumes staight runs with no bends and smooth walls.
Conduit Dimension |  |  |  | Number of Cables
|  |  |  | 100-912 Cat 7A Plus S/FTP (1200 MHz) | 100-910 Cat 7A S/FTP (1000 MHz) | 100-189 Cat 6A U/UTP | 100-196 Cat 6 A F/FTP "S" Foil | 100-191 Cat 6 A U/FTP "S" Foil | 100-914 Cat 6A S/FTP | 190-071-500 Cat 6 U/UTP (B2ca) | 100-071 Cat 6 U/UTP | 100-076 Cat 6 F/UTP | 100-080 Cat6 RD U/UTP | 100-609 Residential Category 6 U/UTP | 100-066 Cat 5e U/UTP | 100-217 Cat 5e F/UTP
Inside Diameter | 25 | mm | Diameter of Cable | 8.5 | 7.8 | 8.3 | 6.9 | 6.7 | 7.5 | 6.5 | 6.2 | 7.6 | 5.4 | 4.6 | 5.2 | 6.4
Spare Capacity | 10 | % | Area of Cable | 56.745 | 47.7836 | 54.1061 | 37.3928 | 35.2565 | 44.1786 | 33.1831 | 30.1907 | 45.3646 | 22.9022 | 16.619 | 21.2372 | 32.1699
Area of Containment | 491 | mm² | Number of Cables | 2 | 3 | 2 | 4 | 4 | 3 | 4 | 5 | 3 | 7 | 10 | 7 | 5
Usable area | 179 | mm²
Only edit blue cells
| This spreadsheet is for information only. Based on BICSI TDMM | [10 empty] | Rev 6: October 2018
NOTE: Accurate at time of publication, higher Euroclass levels of unscreened cables are typically slightly larger in OD so please check Specification Sheets.

## Separation Distances
Separation Distances | [5 empty] | a | b | c | d
This spreadsheet offers guidance for the general separation distances required between copper data cabling and mains power to mitigate the effects of Electromagnetic Interference (EMI). The installer shall additional ensure that all local and national legislation reagading electrical separation shall be complied with. |  |  |  | Segregation Classification - Cable |  | None | Open metalic containment | Perforated metalic containment | Solid metalic containment
[6 empty] | 1 | 2 | 3 | 4
Only edit blue cells (drop down) | [5 empty] | Applicable to plastic containment | Equivalent to weld mesh 50 mm x 100 mm and steel tray of less than 1 mm thickness (and trunking without lid). | Equivalent to steel tray of 1 mm thickness (and trunking without lid). Cables to be installed at least 10 mm below top of barrier. | Equivalent to steel conduit 1.5mm wall thickness. Steel conduit less than 1.5mm thickness will require greater separation.
Reference: EN 50174-2:2018 |  |  |  | Coaxial | 1 | 300 | 225 | 150 | 0
|  |  |  | Unscreened - Cat 5e, 6, 6a | 2 | 100 | 75 | 50 | 0
|  |  |  | Screened - Cat 5e, 6, 6a | 3 | 50 | 38 | 25 | 0
Data cable type | Cat 7 & 7a | Please see note ** below | 4 | Cat 7 & 7a | 4 | 10 | 8 | 5 | 0
[6 empty] | Coaxial | Unscreened - Cat 5e, 6, 6a | Screened - Cat 5e, 6, 6a | Cat 7 & 7a
[6 empty] | 1 | 2 | 3 | 4
Note
Containment (applied to Data or Power cabling) | Open metalic containment | Equivalent to weld mesh 50 mm x 100 mm and steel tray of less than 1 mm thickness (and trunking without lid). | 2 | Qty of Power Circuits | P
|  |  |  | 1 to 3 | 0.2
|  |  |  | 4 to 6 | 0.4
|  | Note |  | 7 to 9 | 0.6
Quantity of Power Circuits | 10 to 12 | 3-phase cables shall be treated as 3 off 1-phase cables. | 0.8 | 10 to 12 | 0.8
|  | More than 20 A shall be treated as multiples of 20 A. |  | 13 to 15 | 1
|  | Lower voltage AC or DC power supply cables shall be treated based upon the their current ratings, i.e. a 100 A 50 V DC cable = 5 of 20 A cables |  | 16 to 30 | 2
|  |  |  | 31 to 45 | 3
|  |  |  | 46 to 60 | 4
|  |  |  | 61 to 75 | 5
Minimum separation distance | 6.4 mm |  |  | > 75 | 6
Only edit blue cells (drop down)
This spreadsheet is for information only. Based on EN 50174-2:2018 |  | Rev 6: October 2018
**Note: Cat 7 and 7a cables relate to Type 1 for Coupling Attenuation, as referenced in IEC61156-5 ed.2.1, 100-914 Category 6A S/FTP also falls into this group