## Data
| Cable Data (Eland, Batt, Prysmian) | [7 empty] | Containment Data (Legrand) | [9 empty] | Lists
Weight (kg/m)
| Cable Type | Core | Size | Nominal Diameter | Weight (kg/m) | Cable Arrangement | Cleat Size | Minimum Bending Radius | Containment Type | Duty | Width | Height | Hot Dip Galv | Deep Galv | Stainless Steel | Pre-galv | Powder coated
BS6724 - Cu/XLPE/LSZH/SWA/LSZH (0.6/1kV) | Cu/XLPE/LSZH/AWA/LSZH | 1c | 50mm | 17.5 | 0.8 | Single |  | 140 | Cable Tray | Heavy Duty | 75 | 50 | 1.4 | 1.484 | 1.316 | 1.344 | 1.358 |  | Containment type | Cable specification | cores | size | containment duty | containment sizes | Arrangement
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 70mm | 20.2 | 0.96 | Single |  | 161.6 | Cable Tray | Heavy Duty | 100 | 50 | 1.5 | 1.59 | 1.41 | 1.44 | 1.455 |  | Cable Tray | Cu/XLPE/PVC/AWA/PVC | 1c | 1.5mm | Heavy Duty | 75 | Single
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 95mm | 22.3 | 1.24 | Single |  | 178.4 | Cable Tray | Heavy Duty | 150 | 50 | 2 | 2.12 | 1.88 | 1.92 | 1.94 |  | Cable Ladder | Cu/XLPE/PVC/SWA/PVC | 2c | 2.5mm | Extra Heavy Duty | 100 | Trefoil
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 120mm | 24.2 | 1.51 | Single |  | 193.6 | Cable Tray | Heavy Duty | 225 | 50 | 3 | 3.18 | 2.82 | 2.88 | 2.91 |  |  | Cu/XLPE/LSZH/AWA/LSZH | 3c | 4mm |  | 150 | Quadcleat
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 150mm | 27.4 | 1.9 | Single |  | 219.2 | Cable Tray | Heavy Duty | 300 | 50 | 3.6 | 3.816 | 3.384 | 3.456 | 3.492 |  |  | Cu/XLPE/LSZH/SWA/LSZH | 4c | 6mm |  | 225
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 185mm | 30 | 2.32 | Single | 60 | 240 | Cable Tray | Heavy Duty | 450 | 50 | 5.9 | 6.254 | 5.546 | 5.664 | 5.723 |  |  | Cu/LSZH 6491B (CPC) | 5c | 10mm |  | 300
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 240mm | 32.8 | 2.93 | Single | 60 | 262.4 | Cable Tray | Heavy Duty | 600 | 50 | 7.6 | 8.056 | 7.144 | 7.296 | 7.372 |  |  | Cu/XLPE/LSZH | 7c | 16mm |  | 450
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 300mm | 35.6 | 3.58 | Single | 60 | 284.8 | Cable Tray | Heavy Duty | 750 | 50 | 12 | 12.72 | 11.28 | 11.52 | 11.64 |  |  | Cu/LSZH/LSZH | 12c | 25mm |  | 600
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 400mm | 40.5 | 4.6 | Single | 63 | 324 | Cable Tray | Heavy Duty | 900 | 50 | 14 | 14.84 | 13.16 | 13.44 | 13.58 |  |  | FP400 | 19c | 35mm |  | 750
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 500mm | 44.2 | 5.77 | Single | 72 | 353.6 | Cable Tray | Extra Heavy Duty | 100 | 80 | 9 | 9.54 | 8.46 | - | - |  |  | FP600S | 27c | 50mm |  | 900
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 630mm | 48.8 | 7.25 | Single | 72 | 390.4 | Cable Tray | Extra Heavy Duty | 150 | 80 | 10.2 | 10.812 | 9.588 | - | - |  |  | N2XH Enhanced Flex | 37c | 70mm
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 800mm | 55.4 | 9.381 | Single | 85 | 443.2 | Cable Tray | Extra Heavy Duty | 225 | 80 | 13 | 13.78 | 12.22 | - | - |  |  | - |  | 95mm
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 1000mm | 60.6 | 11.54 | Single | 96 | 484.8 | Cable Tray | Extra Heavy Duty | 300 | 80 | 15.3 | 16.218 | 14.382 | - | - |  |  | - |  | 120mm
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 50mm | 17.5 | 0.8 | Quadcleat | N/A | 140 | Cable Tray | Extra Heavy Duty | 450 | 80 | 26.4 | 27.984 | 24.816 | - | - |  |  | - |  | 150mm
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 70mm | 20.2 | 0.96 | Quadcleat | N/A | 161.6 | Cable Tray | Extra Heavy Duty | 600 | 80 | 32.5 | 34.45 | 30.55 | - | - |  |  | - |  | 185mm
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 95mm | 22.3 | 1.24 | Quadcleat | N/A | 178.4 | Cable Ladder | Heavy Duty | 150 | 125 | 13.8 | 14.766 | 12.972 | - | 13.386 |  |  | - |  | 240mm
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 120mm | 24.2 | 1.51 | Quadcleat | 17 | 193.6 | Cable Ladder | Heavy Duty | 300 | 125 | 15 | 16.05 | 14.1 | - | 14.55 |  |  | - |  | 300mm
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 150mm | 27.4 | 1.9 | Quadcleat | 17.5 | 219.2 | Cable Ladder | Heavy Duty | 450 | 125 | 16.3 | 17.441 | 15.322 | - | 15.811 |  |  | - |  | 400mm
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 185mm | 30 | 2.32 | Quadcleat | 19.5 | 240 | Cable Ladder | Heavy Duty | 600 | 125 | 18.5 | 19.795 | 17.39 | - | 17.945 |  |  | - |  | 500mm
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 240mm | 32.8 | 2.93 | Quadcleat | 22.5 | 262.4 | Cable Ladder | Heavy Duty | 750 | 125 | 22 | 23.54 | 20.68 | - | 21.34 |  |  | - |  | 630mm
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 300mm | 35.6 | 3.58 | Quadcleat | 25.75 | 284.8 | Cable Ladder | Heavy Duty | 900 | 125 | 23.9 | 25.573 | 22.466 | - | 23.183 |  |  | - |  | 800mm
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 400mm | 40.5 | 4.6 | Quadcleat | 25.75 | 324 | Cable Ladder | Extra Heavy Duty | 150 | 150 | 20.7 | 22.149 | 19.458 | - | 20.079 |  |  | - |  | 1000mm
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 500mm | 44.2 | 5.77 | Quadcleat | 30 | 353.6 | Cable Ladder | Extra Heavy Duty | 300 | 150 | 22.1 | 23.647 | 20.774 | - | 21.437
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 630mm | 48.8 | 7.25 | Quadcleat | 30.25 | 390.4 | Cable Ladder | Extra Heavy Duty | 450 | 150 | 23.5 | 25.145 | 22.09 | - | 22.795
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 800mm | 55.4 | 9.381 | Quadcleat | 35 | 443.2 | Cable Ladder | Extra Heavy Duty | 600 | 150 | 25 | 26.75 | 23.5 | - | 24.25
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 1000mm | 60.6 | 11.54 | Quadcleat | 37.5 | 484.8 | Cable Ladder | Extra Heavy Duty | 750 | 150 | 28.8 | 30.816 | 27.072 | - | 27.936
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 50mm | 17.5 | 0.8 | Trefoil | N/A | 140 | Cable Ladder | Extra Heavy Duty | 900 | 150 | 30.8 | 32.956 | 28.952 | - | 29.876 |  |  | Override empty slots with new cable type. Must match cable type within Cable Data table.
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 70mm | 20.2 | 0.96 | Trefoil | 20 | 161.6
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 95mm | 22.3 | 1.24 | Trefoil | 20 | 178.4
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 120mm | 24.2 | 1.51 | Trefoil | 21 | 193.6 | [9 empty] | Trefoil Cable Range Cleats (Vulcan) | [7 empty] | Maximum Safe Loading - Tray (Legrand) | Maximum Safe Loading - Ladder (Legrand)
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 150mm | 27.4 | 1.9 | Trefoil | 24 | 219.2 | [12 empty] | Dimensions
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 185mm | 30 | 2.32 | Trefoil | 26.3333 | 240 | [9 empty] | Part No. | Min Dia | Max Dia | W | H | D | kg
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 240mm | 32.8 | 2.93 | Trefoil | 28.3333 | 262.4 | [9 empty] | VRT+00 | 19 | 24 | 60 | 93 | 54 | 0.251
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 300mm | 35.6 | 3.58 | Trefoil | 28.3333 | 284.8 | [9 empty] | VRT+01 | 23 | 28 | 63 | 98 | 54 | 0.258
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 400mm | 40.5 | 4.6 | Trefoil | 35 | 324 | [9 empty] | VRT+02 | 27 | 32 | 72 | 106 | 54 | 0.269
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 500mm | 44.2 | 5.77 | Trefoil | 37.3333 | 353.6 | [9 empty] | VRT+03 | 30 | 35 | 79 | 112 | 54 | 0.279
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 630mm | 48.8 | 7.25 | Trefoil | 40.3333 | 390.4 | [9 empty] | VRT+04 | 33 | 38 | 85 | 118 | 54 | 0.284
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 800mm | 55.4 | 9.381 | Trefoil | 44.6667 | 443.2 | [9 empty] | VRT+05 | 36 | 42 | 96 | 125 | 54 | 0.319
| Cu/XLPE/LSZH/AWA/LSZH | 1c | 1000mm | 60.6 | 11.54 | Trefoil | 47.6667 | 484.8 | [9 empty] | VRT+06 | 40 | 46 | 105 | 133 | 54 | 0.331
| Cu/XLPE/LSZH/SWA/LSZH | 2c | 1.5mm | 12.1 | 0.302 | Single |  | 72.6 | [9 empty] | VRT+07 | 44 | 50 | 112 | 140 | 54 | 0.391
| Cu/XLPE/LSZH/SWA/LSZH | 2c | 2.5mm | 13.6 | 0.346 | Single |  | 81.6 | [9 empty] | VRT+08 | 48 | 55 | 121 | 149 | 54 | 0.405
| Cu/XLPE/LSZH/SWA/LSZH | 2c | 4mm | 14.7 | 0.41 | Single |  | 88.2 | [9 empty] | VRT+09 | 51 | 58 | 126 | 154 | 54 | 0.411
| Cu/XLPE/LSZH/SWA/LSZH | 2c | 6mm | 15.9 | 0.499 | Single |  | 95.4 | [9 empty] | VRT+10 | 55 | 62 | 134 | 162 | 54 | 0.442
| Cu/XLPE/LSZH/SWA/LSZH | 2c | 10mm | 18 | 0.648 | Single |  | 108 | [9 empty] | VRT+11 | 59 | 66 | 143 | 170 | 54 | 0.453
| Cu/XLPE/LSZH/SWA/LSZH | 2c | 16mm | 20.4 | 0.978 | Single |  | 122.4 | [9 empty] | VRT+12 | 63 | 70 | 152 | 177 | 54 | 0.46
| Cu/XLPE/LSZH/SWA/LSZH | 2c | 25mm | 20.4 | 1.29 | Single |  | 163.2 | [9 empty] | VRT+13 | 67 | 74 | 161 | 185 | 54 | 0.524
| Cu/XLPE/LSZH/SWA/LSZH | 2c | 35mm | 23.3 | 1.5 | Single |  | 186.4 | [9 empty] | VRT+14 | 71 | 78 | 169 | 192 | 54 | 0.536
| Cu/XLPE/LSZH/SWA/LSZH | 2c | 50mm | 25.8 | 1.89 | Single |  | 206.4 | [9 empty] | VRT+15 | 74 | 82 | 176 | 199 | 54 | 0.542
| Cu/XLPE/LSZH/SWA/LSZH | 2c | 70mm | 29 | 2.45 | Single |  | 232 | [9 empty] | VRT+16 | 77 | 85 | 183 | 205 | 54 | 0.544
| Cu/XLPE/LSZH/SWA/LSZH | 2c | 95mm | 33.1 | 3.3 | Single | 60 | 264.8 | [9 empty] | VRT+17 | 81 | 89 | 190 | 216 | 54 | 0.618
| Cu/XLPE/LSZH/SWA/LSZH | 2c | 120mm | 39.3 | 4.02 | Single | 63 | 314.4 | [9 empty] | VRT+18 | 85 | 93 | 200 | 225 | 54 | 0.628
| Cu/XLPE/LSZH/SWA/LSZH | 2c | 150mm | 39.3 | 4.75 | Single | 63 | 314.4 | [9 empty] | VRT+19 | 89 | 97 | 200 | 235 | 54 | 0.637
| Cu/XLPE/LSZH/SWA/LSZH | 3c | 1.5mm | 12.6 | 0.33 | Single |  | 75.6 | [9 empty] | VRT+20 | 93 | 101 | 215 | 240 | 54 | 0.646
| Cu/XLPE/LSZH/SWA/LSZH | 3c | 2.5mm | 14.1 | 0.39 | Single |  | 84.6
| Cu/XLPE/LSZH/SWA/LSZH | 3c | 4mm | 15.3 | 0.464 | Single |  | 91.8 | [9 empty] | Single Cable Range Cleats (Vulcan)
| Cu/XLPE/LSZH/SWA/LSZH | 3c | 6mm | 16.6 | 0.568 | Single |  | 99.6 | [12 empty] | Dimensions
| Cu/XLPE/LSZH/SWA/LSZH | 3c | 10mm | 19.5 | 0.866 | Single |  | 117 | [9 empty] | Part No. | Min Dia | Max Dia | W | H | D | kg
| Cu/XLPE/LSZH/SWA/LSZH | 3c | 16mm | 21.6 | 1.152 | Single |  | 129.6 | [9 empty] | VRT+00 | 30 | 42 | 60 | 93 | 54 | 0.251
| Cu/XLPE/LSZH/SWA/LSZH | 3c | 25mm | 23.6 | 1.8 | Single |  | 188.8 | [9 empty] | VRT+01 | 38 | 50 | 63 | 98 | 54 | 0.258
| Cu/XLPE/LSZH/SWA/LSZH | 3c | 35mm | 25.7 | 2.23 | Single |  | 205.6 | [9 empty] | VRT+02 | 43 | 58 | 72 | 106 | 54 | 0.269
| Cu/XLPE/LSZH/SWA/LSZH | 3c | 50mm | 28.5 | 2.49 | Single |  | 228 | [9 empty] | VRT+03 | 49 | 64 | 79 | 112 | 54 | 0.279
| Cu/XLPE/LSZH/SWA/LSZH | 3c | 70mm | 32.2 | 3.29 | Single | 60 | 257.6 | [9 empty] | VRT+04 | 55 | 70 | 85 | 118 | 54 | 0.284
| Cu/XLPE/LSZH/SWA/LSZH | 3c | 95mm | 37 | 4.44 | Single | 60 | 296 | [9 empty] | VRT+05 | 58 | 75 | 96 | 125 | 54 | 0.319
| Cu/XLPE/LSZH/SWA/LSZH | 3c | 120mm | 40.4 | 5.47 | Single | 63 | 323.2 | [9 empty] | VRT+06 | 63 | 84 | 105 | 133 | 54 | 0.331
| Cu/XLPE/LSZH/SWA/LSZH | 3c | 150mm | 45.5 | 6.93 | Single | 63 | 364 | [9 empty] | VRT+07 | 73 | 90 | 112 | 140 | 54 | 0.391
| Cu/XLPE/LSZH/SWA/LSZH | 4c | 1.5mm | 13.5 | 0.365 | Single |  | 81 | [9 empty] | VRT+08 | 83 | 100 | 121 | 149 | 54 | 0.405
| Cu/XLPE/LSZH/SWA/LSZH | 4c | 2.5mm | 15 | 0.438 | Single |  | 90 | [9 empty] | VRT+09 | 86 | 104 | 126 | 154 | 54 | 0.411
| Cu/XLPE/LSZH/SWA/LSZH | 4c | 4mm | 16.4 | 0.532 | Single |  | 98.4 | [9 empty] | VRT+10 | 88 | 110 | 134 | 162 | 54 | 0.442
| Cu/XLPE/LSZH/SWA/LSZH | 4c | 6mm | 18.7 | 0.764 | Single |  | 112.2 | [9 empty] | VRT+11 | 90 | 115 | 143 | 170 | 54 | 0.453
| Cu/XLPE/LSZH/SWA/LSZH | 4c | 10mm | 21.1 | 1.013 | Single |  | 126.6 | [9 empty] | VRT+12 | 100 | 125 | 152 | 177 | 54 | 0.46
| Cu/XLPE/LSZH/SWA/LSZH | 4c | 16mm | 23.4 | 1.36 | Single |  | 140.4 | [9 empty] | VRT+13 | 107 | 132 | 161 | 185 | 54 | 0.524
| Cu/XLPE/LSZH/SWA/LSZH | 4c | 25mm | 26.1 | 2.16 | Single |  | 208.8 | [9 empty] | VRT+14 | 120 | 145 | 169 | 192 | 54 | 0.536
| Cu/XLPE/LSZH/SWA/LSZH | 4c | 35mm | 28.6 | 2.69 | Single |  | 228.8 | [9 empty] | VRT+15 | 125 | 150 | 176 | 199 | 54 | 0.542
| Cu/XLPE/LSZH/SWA/LSZH | 4c | 50mm | 32 | 3.13 | Single | 60 | 256 | [9 empty] | VRT+16 | 132 | 153 | 183 | 205 | 54 | 0.544
| Cu/XLPE/LSZH/SWA/LSZH | 4c | 70mm | 37.7 | 4.5 | Single | 60 | 301.6 | [9 empty] | VRT+17 | 136 | 156 | 190 | 216 | 54 | 0.618
| Cu/XLPE/LSZH/SWA/LSZH | 4c | 95mm | 41.7 | 5.6 | Single | 63 | 333.6 | [9 empty] | VRT+18 | 139 | 159 | 200 | 225 | 54 | 0.628
| Cu/XLPE/LSZH/SWA/LSZH | 4c | 120mm | 47.1 | 7.4 | Single | 72 | 376.8 | [9 empty] | VRT+19 | 142 | 162 | 200 | 235 | 54 | 0.637
| Cu/XLPE/LSZH/SWA/LSZH | 4c | 150mm | 51.4 | 8.78 | Single | 79 | 411.2 | [9 empty] | VRT+20 | 150 | 170 | 215 | 240 | 54 | 0.646
| Cu/XLPE/LSZH/SWA/LSZH | 4c | 185mm | 56.6 | 10.63 | Single | 85 | 452.8
| Cu/XLPE/LSZH/SWA/LSZH | 4c | 240mm | 63 | 13.39 | Single | 105 | 504 | [9 empty] | Quad Cable Range Cleats (Vulcan)
| Cu/XLPE/LSZH/SWA/LSZH | 4c | 300mm | 63.6 | 14.998 | Single | 105 | 508.8 | [12 empty] | Dimensions
| Cu/XLPE/LSZH/SWA/LSZH | 5c | 1.5mm | 14.3 | 0.41 | Single |  | 85.8 | [9 empty] | Part No. | Min Dia | Max Dia | W | H | D | kg
| Cu/XLPE/LSZH/SWA/LSZH | 5c | 2.5mm | 16.3 | 0.47 | Single |  | 97.8 | [9 empty] | VRQ+01 | 23 | 25 | 68 | 110 | 54 | 0.284
| Cu/XLPE/LSZH/SWA/LSZH | 5c | 4mm | 17.8 | 0.71 | Single |  | 106.8 | [9 empty] | VRQ+02 | 26 | 27 | 70 | 113 | 54 | 0.286
| Cu/XLPE/LSZH/SWA/LSZH | 5c | 6mm | 20 | 0.876 | Single |  | 120 | [9 empty] | VRQ+03 | 28 | 31 | 78 | 128 | 54 | 0.318
| Cu/XLPE/LSZH/SWA/LSZH | 5c | 10mm | 22.9 | 1.165 | Single |  | 137.4 | [9 empty] | VRQ+3A | 31 | 35 | 90 | 138 | 54 | 0.35
| Cu/XLPE/LSZH/SWA/LSZH | 5c | 16mm | 26.6 | 1.742 | Single |  | 159.6 | [9 empty] | VRQ+04 | 35 | 42 | 103 | 148 | 54 | 0.378
| Cu/XLPE/LSZH/SWA/LSZH | 5c | 25mm | 31.5 | 2.323 | Single | 60 | 252 | [9 empty] | VRQ+05 | 43 | 47 | 120 | 165 | 54 | 0.452
| Cu/XLPE/LSZH/SWA/LSZH | 5c | 35mm | 34.8 | 2.932 | Single | 60 | 278.4 | [9 empty] | VRQ+06 | 48 | 50 | 121 | 170 | 54 | 0.467
| Cu/XLPE/LSZH/SWA/LSZH | 5c | 50mm | 40.4 | 4.192 | Single | 63 | 323.2 | [9 empty] | VRQ+07 | 51 | 57 | 140 | 190 | 54 | 0.486
| Cu/XLPE/LSZH/SWA/LSZH | 7c | 1.5mm | 15.2 | 0.47 | Single |  | 91.2 | [9 empty] | VRQ+08 | 58 | 63 | 150 | 200 | 54 | 0.499
| Cu/XLPE/LSZH/SWA/LSZH | 7c | 2.5mm | 17.1 | 0.6 | Single |  | 102.6 | [9 empty] | VRQ+09 | 64 | 70 | 170 | 218 | 54 | 0.58
| Cu/XLPE/LSZH/SWA/LSZH | 12c | 1.5mm | 19.4 | 0.78 | Single |  | 116.4
| Cu/XLPE/LSZH/SWA/LSZH | 12c | 2.5mm | 22.4 | 1 | Single |  | 134.4
| Cu/XLPE/LSZH/SWA/LSZH | 19c | 1.5mm | 22.2 | 1 | Single |  | 133.2
| Cu/XLPE/LSZH/SWA/LSZH | 19c | 2.5mm | 26.6 | 1.54 | Single |  | 159.6 | [9 empty] | Radius bends (Legrand)
| Cu/XLPE/LSZH/SWA/LSZH | 27c | 1.5mm | 26.7 | 1.5 | Single |  | 160.2
| Cu/XLPE/LSZH/SWA/LSZH | 27c | 2.5mm | 30.7 | 1.95 | Single | 60 | 184.2 | [9 empty] | Type | Width | Radius
| Cu/XLPE/LSZH/SWA/LSZH | 37c | 1.5mm | 29 | 1.8 | Single |  | 174 | [9 empty] | Ladder | 150 | 300
| Cu/XLPE/LSZH/SWA/LSZH | 37c | 2.5mm | 33.8 | 2.35 | Single | 60 | 202.8 | [9 empty] | Ladder | 150 | 450
BS5467 - Cu/XLPE/PVC/AWA/PVC (0.6/1kV) & Cu/XLPE/PVC/SWA/PVC | Cu/XLPE/PVC/AWA/PVC | 1c | 50mm | 17.5 | 0.8 | Single |  | 140 | [9 empty] | Ladder | 150 | 600
| Cu/XLPE/PVC/AWA/PVC | 1c | 70mm | 20.2 | 0.96 | Single |  | 161.6 | [9 empty] | Ladder | 150 | 750
| Cu/XLPE/PVC/AWA/PVC | 1c | 95mm | 22.3 | 1.24 | Single |  | 178.4 | [9 empty] | Ladder | 150 | 900
| Cu/XLPE/PVC/AWA/PVC | 1c | 120mm | 24.2 | 1.51 | Single |  | 193.6 | [9 empty] | Ladder | 300 | 300
| Cu/XLPE/PVC/AWA/PVC | 1c | 150mm | 27.4 | 1.9 | Single |  | 219.2 | [9 empty] | Ladder | 300 | 450
| Cu/XLPE/PVC/AWA/PVC | 1c | 185mm | 30 | 2.32 | Single | 60 | 240 | [9 empty] | Ladder | 300 | 600
| Cu/XLPE/PVC/AWA/PVC | 1c | 240mm | 32.8 | 2.93 | Single | 60 | 262.4 | [9 empty] | Ladder | 300 | 750
| Cu/XLPE/PVC/AWA/PVC | 1c | 300mm | 35.6 | 3.58 | Single | 60 | 284.8 | [9 empty] | Ladder | 300 | 900
| Cu/XLPE/PVC/AWA/PVC | 1c | 400mm | 40.5 | 4.6 | Single | 63 | 324 | [9 empty] | Ladder | 450 | 300
| Cu/XLPE/PVC/AWA/PVC | 1c | 500mm | 44.2 | 5.77 | Single | 72 | 353.6 | [9 empty] | Ladder | 450 | 450
| Cu/XLPE/PVC/AWA/PVC | 1c | 630mm | 48.8 | 7.25 | Single | 72 | 390.4 | [9 empty] | Ladder | 450 | 600
| Cu/XLPE/PVC/AWA/PVC | 1c | 800mm | 55.4 | 9.381 | Single | 85 | 443.2 | [9 empty] | Ladder | 450 | 750
| Cu/XLPE/PVC/AWA/PVC | 1c | 1000mm | 60.6 | 11.54 | Single | 96 | 484.8 | [9 empty] | Ladder | 450 | 900
| Cu/XLPE/PVC/AWA/PVC | 1c | 50mm | 17.5 | 0.8 | Quadcleat | N/A | 140 | [9 empty] | Ladder | 600 | 300
| Cu/XLPE/PVC/AWA/PVC | 1c | 70mm | 20.2 | 0.96 | Quadcleat | N/A | 161.6 | [9 empty] | Ladder | 600 | 450
| Cu/XLPE/PVC/AWA/PVC | 1c | 95mm | 22.3 | 1.24 | Quadcleat | N/A | 178.4 | [9 empty] | Ladder | 600 | 600
| Cu/XLPE/PVC/AWA/PVC | 1c | 120mm | 24.2 | 1.51 | Quadcleat | 17 | 193.6 | [9 empty] | Ladder | 600 | 750
| Cu/XLPE/PVC/AWA/PVC | 1c | 150mm | 27.4 | 1.9 | Quadcleat | 17.5 | 219.2 | [9 empty] | Ladder | 600 | 900
| Cu/XLPE/PVC/AWA/PVC | 1c | 185mm | 30 | 2.32 | Quadcleat | 19.5 | 240 | [9 empty] | Ladder | 750 | 300
| Cu/XLPE/PVC/AWA/PVC | 1c | 240mm | 32.8 | 2.93 | Quadcleat | 22.5 | 262.4 | [9 empty] | Ladder | 750 | 450
| Cu/XLPE/PVC/AWA/PVC | 1c | 300mm | 35.6 | 3.58 | Quadcleat | 25.75 | 284.8 | [9 empty] | Ladder | 750 | 600
| Cu/XLPE/PVC/AWA/PVC | 1c | 400mm | 40.5 | 4.6 | Quadcleat | 25.75 | 324 | [9 empty] | Ladder | 750 | 750
| Cu/XLPE/PVC/AWA/PVC | 1c | 500mm | 44.2 | 5.77 | Quadcleat | 30 | 353.6 | [9 empty] | Ladder | 750 | 900
| Cu/XLPE/PVC/AWA/PVC | 1c | 630mm | 48.8 | 7.25 | Quadcleat | 30.25 | 390.4 | [9 empty] | Ladder | 900 | 300
| Cu/XLPE/PVC/AWA/PVC | 1c | 800mm | 55.4 | 9.381 | Quadcleat | 35 | 443.2 | [9 empty] | Ladder | 900 | 450
| Cu/XLPE/PVC/AWA/PVC | 1c | 1000mm | 60.6 | 11.54 | Quadcleat | 37.5 | 484.8 | [9 empty] | Ladder | 900 | 600
| Cu/XLPE/PVC/AWA/PVC | 1c | 50mm | 17.5 | 0.8 | Trefoil | N/A | 140 | [9 empty] | Ladder | 900 | 750
| Cu/XLPE/PVC/AWA/PVC | 1c | 70mm | 20.2 | 0.96 | Trefoil | 20 | 161.6 | [9 empty] | Ladder | 900 | 900
| Cu/XLPE/PVC/AWA/PVC | 1c | 95mm | 22.3 | 1.24 | Trefoil | 20 | 178.4 | [9 empty] | Tray | 100 to 300 | 180
| Cu/XLPE/PVC/AWA/PVC | 1c | 120mm | 24.2 | 1.51 | Trefoil | 21 | 193.6 | [9 empty] | Tray | 450 and 600 | 240
| Cu/XLPE/PVC/AWA/PVC | 1c | 150mm | 27.4 | 1.9 | Trefoil | 24 | 219.2
| Cu/XLPE/PVC/AWA/PVC | 1c | 185mm | 30 | 2.32 | Trefoil | 26.3333 | 240
| Cu/XLPE/PVC/AWA/PVC | 1c | 240mm | 32.8 | 2.93 | Trefoil | 28.3333 | 262.4
| Cu/XLPE/PVC/AWA/PVC | 1c | 300mm | 35.6 | 3.58 | Trefoil | 28.3333 | 284.8
| Cu/XLPE/PVC/AWA/PVC | 1c | 400mm | 40.5 | 4.6 | Trefoil | 35 | 324
| Cu/XLPE/PVC/AWA/PVC | 1c | 500mm | 44.2 | 5.77 | Trefoil | 37.3333 | 353.6
| Cu/XLPE/PVC/AWA/PVC | 1c | 630mm | 48.8 | 7.25 | Trefoil | 40.3333 | 390.4
| Cu/XLPE/PVC/AWA/PVC | 1c | 800mm | 55.4 | 9.381 | Trefoil | 44.6667 | 443.2
| Cu/XLPE/PVC/AWA/PVC | 1c | 1000mm | 60.6 | 11.54 | Trefoil | 47.6667 | 484.8
| Cu/XLPE/PVC/SWA/PVC | 2c | 1.5mm | 12.1 | 0.302 | Single |  | 72.6
| Cu/XLPE/PVC/SWA/PVC | 2c | 2.5mm | 13.6 | 0.346 | Single |  | 81.6
| Cu/XLPE/PVC/SWA/PVC | 2c | 4mm | 14.7 | 0.41 | Single |  | 88.2
| Cu/XLPE/PVC/SWA/PVC | 2c | 6mm | 15.9 | 0.499 | Single |  | 95.4
| Cu/XLPE/PVC/SWA/PVC | 2c | 10mm | 18 | 0.648 | Single |  | 108
| Cu/XLPE/PVC/SWA/PVC | 2c | 16mm | 20.4 | 0.978 | Single |  | 122.4
| Cu/XLPE/PVC/SWA/PVC | 2c | 25mm | 20.4 | 1.29 | Single |  | 163.2
| Cu/XLPE/PVC/SWA/PVC | 2c | 35mm | 23.3 | 1.5 | Single |  | 186.4
| Cu/XLPE/PVC/SWA/PVC | 2c | 50mm | 25.8 | 1.89 | Single |  | 206.4
| Cu/XLPE/PVC/SWA/PVC | 2c | 70mm | 29 | 2.5 | Single |  | 232
| Cu/XLPE/PVC/SWA/PVC | 2c | 95mm | 33.1 | 3.3 | Single | 60 | 264.8
| Cu/XLPE/PVC/SWA/PVC | 2c | 120mm | 36.1 | 4.02 | Single | 63 | 288.8
| Cu/XLPE/PVC/SWA/PVC | 2c | 150mm | 39.3 | 4.75 | Single | 63 | 314.4
| Cu/XLPE/PVC/SWA/PVC | 3c | 1.5mm | 12.6 | 0.33 | Single |  | 75.6
| Cu/XLPE/PVC/SWA/PVC | 3c | 2.5mm | 14.1 | 0.39 | Single |  | 84.6
| Cu/XLPE/PVC/SWA/PVC | 3c | 4mm | 15.3 | 0.464 | Single |  | 91.8
| Cu/XLPE/PVC/SWA/PVC | 3c | 6mm | 16.6 | 0.568 | Single |  | 99.6
| Cu/XLPE/PVC/SWA/PVC | 3c | 10mm | 19.5 | 0.866 | Single |  | 117
| Cu/XLPE/PVC/SWA/PVC | 3c | 16mm | 21.6 | 1.152 | Single |  | 129.6
| Cu/XLPE/PVC/SWA/PVC | 3c | 25mm | 23.6 | 1.8 | Single |  | 188.8
| Cu/XLPE/PVC/SWA/PVC | 3c | 35mm | 25.7 | 2.23 | Single |  | 205.6
| Cu/XLPE/PVC/SWA/PVC | 3c | 50mm | 28.5 | 2.49 | Single |  | 228
| Cu/XLPE/PVC/SWA/PVC | 3c | 70mm | 32.2 | 3.29 | Single | 60 | 257.6
| Cu/XLPE/PVC/SWA/PVC | 3c | 95mm | 37 | 4.44 | Single | 60 | 296
| Cu/XLPE/PVC/SWA/PVC | 3c | 120mm | 40.4 | 5.47 | Single | 63 | 323.2
| Cu/XLPE/PVC/SWA/PVC | 3c | 150mm | 45.5 | 6.93 | Single | 72 | 364
| Cu/XLPE/PVC/SWA/PVC | 3c | 185mm | 49.8 | 8.35 | Single | 79 | 398.4
| Cu/XLPE/PVC/SWA/PVC | 3c | 240mm | 55.1 | 10.4 | Single | 85 | 440.8
| Cu/XLPE/PVC/SWA/PVC | 3c | 300mm | 60.2 | 12.6 | Single | 96 | 481.6
| Cu/XLPE/PVC/SWA/PVC | 3c | 400mm | 66.6 | 14.6 | Single | 105 | 532.8
| Cu/XLPE/PVC/SWA/PVC | 4c | 1.5mm | 13.3 | 0.365 | Single |  | 79.8
| Cu/XLPE/PVC/SWA/PVC | 4c | 2.5mm | 15 | 0.438 | Single |  | 90
| Cu/XLPE/PVC/SWA/PVC | 4c | 4mm | 16.4 | 0.532 | Single |  | 98.4
| Cu/XLPE/PVC/SWA/PVC | 4c | 6mm | 18.7 | 0.764 | Single |  | 112.2
| Cu/XLPE/PVC/SWA/PVC | 4c | 10mm | 21.1 | 1.013 | Single |  | 126.6
| Cu/XLPE/PVC/SWA/PVC | 4c | 16mm | 23.4 | 1.36 | Single |  | 140.4
| Cu/XLPE/PVC/SWA/PVC | 4c | 25mm | 26.1 | 2.16 | Single |  | 208.8
| Cu/XLPE/PVC/SWA/PVC | 4c | 35mm | 28.6 | 2.69 | Single |  | 228.8
| Cu/XLPE/PVC/SWA/PVC | 4c | 50mm | 32 | 3.13 | Single | 60 | 256
| Cu/XLPE/PVC/SWA/PVC | 4c | 70mm | 37.7 | 4.5 | Single | 60 | 301.6
| Cu/XLPE/PVC/SWA/PVC | 4c | 95mm | 41.7 | 5.6 | Single | 63 | 333.6
| Cu/XLPE/PVC/SWA/PVC | 4c | 120mm | 47.1 | 7.4 | Single | 72 | 376.8
| Cu/XLPE/PVC/SWA/PVC | 4c | 150mm | 51.4 | 8.78 | Single | 79 | 411.2
| Cu/XLPE/PVC/SWA/PVC | 4c | 185mm | 56.6 | 10.63 | Single | 85 | 452.8
| Cu/XLPE/PVC/SWA/PVC | 4c | 240mm | 63 | 13.39 | Single | 105 | 504
| Cu/XLPE/PVC/SWA/PVC | 4c | 300mm | 68.8 | 16.29 | Single | 105 | 550.4
| Cu/XLPE/PVC/SWA/PVC | 4c | 400mm | 78.1 | 19.8 | Single | 112 | 624.8
| Cu/XLPE/PVC/SWA/PVC | 5c | 1.5mm | 14.3 | 0.41 | Single |  | 85.8
| Cu/XLPE/PVC/SWA/PVC | 5c | 2.5mm | 16.1 | 0.47 | Single |  | 96.6
| Cu/XLPE/PVC/SWA/PVC | 5c | 4mm | 17.8 | 0.71 | Single |  | 106.8
| Cu/XLPE/PVC/SWA/PVC | 5c | 6mm | 20 | 0.876 | Single |  | 120
| Cu/XLPE/PVC/SWA/PVC | 5c | 10mm | 22.9 | 1.165 | Single |  | 137.4
| Cu/XLPE/PVC/SWA/PVC | 5c | 16mm | 26.6 | 1.742 | Single |  | 159.6
| Cu/XLPE/PVC/SWA/PVC | 5c | 25mm | 31.5 | 2.323 | Single | 60 | 252
| Cu/XLPE/PVC/SWA/PVC | 5c | 35mm | 34.8 | 2.932 | Single | 60 | 278.4
| Cu/XLPE/PVC/SWA/PVC | 5c | 50mm | 40.4 | 4.192 | Single | 63 | 323.2
| Cu/XLPE/PVC/SWA/PVC | 7c | 1.5mm | 15.2 | 0.47 | Single |  | 91.2
| Cu/XLPE/PVC/SWA/PVC | 7c | 2.5mm | 17.1 | 0.6 | Single |  | 102.6
| Cu/XLPE/PVC/SWA/PVC | 7c | 4mm | 19.1 | 0.881 | Single |  | 114.6
| Cu/XLPE/PVC/SWA/PVC | 12c | 1.5mm | 19.4 | 0.78 | Single |  | 116.4
| Cu/XLPE/PVC/SWA/PVC | 12c | 2.5mm | 22.4 | 1 | Single |  | 134.4
| Cu/XLPE/PVC/SWA/PVC | 19c | 1.5mm | 22.2 | 1 | Single |  | 133.2
| Cu/XLPE/PVC/SWA/PVC | 19c | 2.5mm | 26.6 | 1.54 | Single |  | 159.6
| Cu/XLPE/PVC/SWA/PVC | 27c | 1.5mm | 26.7 | 1.5 | Single |  | 160.2
| Cu/XLPE/PVC/SWA/PVC | 27c | 2.5mm | 30.7 | 1.95 | Single | 60 | 184.2
| Cu/XLPE/PVC/SWA/PVC | 37c | 1.5mm | 29 | 1.8 | Single |  | 174
| Cu/XLPE/PVC/SWA/PVC | 37c | 2.5mm | 33.8 | 2.35 | Single | 60 | 202.8
6491B / H07Z-R / BS EN 50525-3-41 | Cu/LSZH 6491B (CPC) | 1c | 1.5mm | 3.4 | 0.022 | Single |  | 20.4
| Cu/LSZH 6491B (CPC) | 1c | 2.5mm | 4.1 | 0.035 | Single |  | 24.6
| Cu/LSZH 6491B (CPC) | 1c | 4mm | 4.7 | 0.05 | Single |  | 28.2
| Cu/LSZH 6491B (CPC) | 1c | 6mm | 5.4 | 0.072 | Single |  | 32.4
| Cu/LSZH 6491B (CPC) | 1c | 10mm | 6.8 | 0.121 | Single |  | 40.8
| Cu/LSZH 6491B (CPC) | 1c | 16mm | 8 | 0.182 | Single |  | 48
| Cu/LSZH 6491B (CPC) | 1c | 25mm | 9.8 | 0.285 | Single |  | 78.4
| Cu/LSZH 6491B (CPC) | 1c | 35mm | 10 | 0.39 | Single |  | 80
| Cu/LSZH 6491B (CPC) | 1c | 50mm | 13.2 | 0.51 | Single |  | 105.6
| Cu/LSZH 6491B (CPC) | 1c | 70mm | 15.1 | 0.71 | Single |  | 120.8
| Cu/LSZH 6491B (CPC) | 1c | 95mm | 17 | 0.98 | Single |  | 136
| Cu/LSZH 6491B (CPC) | 1c | 120mm | 19 | 1.22 | Single |  | 152
| Cu/LSZH 6491B (CPC) | 1c | 150mm | 21 | 1.5 | Single |  | 168
| Cu/LSZH 6491B (CPC) | 1c | 185mm | 23.5 | 1.91 | Single |  | 188
| Cu/LSZH 6491B (CPC) | 1c | 240mm | 26.5 | 2.49 | Single |  | 212
| Cu/LSZH 6491B (CPC) | 1c | 300mm | 29.5 | 3.1 | Single |  | 236
| Cu/LSZH 6491B (CPC) | 1c | 400mm | 33.5 | 3.95 | Single | 60 | 268
| Cu/LSZH 6491B (CPC) | 1c | 500mm | 37 | 5 | Single | 60 | 296
| Cu/LSZH 6491B (CPC) | 1c | 630mm | 41 | 6.35 | Single | 63 | 328
BS8573 - Cu/XLPE/LSZH (0.6/1kV) | Cu/XLPE/LSZH | 1c | 50mm | 13 | 0.525 | Single |  | 104
| Cu/XLPE/LSZH | 1c | 70mm | 15.5 | 0.73 | Single |  | 124
| Cu/XLPE/LSZH | 1c | 95mm | 18 | 0.99 | Single |  | 144
| Cu/XLPE/LSZH | 1c | 120mm | 19.5 | 1.23 | Single |  | 156
| Cu/XLPE/LSZH | 1c | 150mm | 32 | 2.15 | Single | 60 | 256
| Cu/XLPE/LSZH | 1c | 185mm | 32 | 2.4 | Single | 60 | 256
| Cu/XLPE/LSZH | 1c | 240mm | 40 | 2.7 | Single | 63 | 320
| Cu/XLPE/LSZH | 1c | 300mm | 40 | 2.95 | Single | 63 | 320
| Cu/XLPE/LSZH | 1c | 400mm | 50 | 3.3 | Single | 79 | 400
| Cu/XLPE/LSZH | 1c | 500mm | 50 | 3.75 | Single | 79 | 400
| Cu/XLPE/LSZH | 1c | 630mm | 50 | 4.2 | Single | 79 | 400
| Cu/XLPE/LSZH | 1c | 800mm | 63 | 4.75 | Single | 105 | 504
| Cu/XLPE/LSZH | 1c | 1000mm | 63 | 5.3 | Single | 105 | 504
| Cu/XLPE/LSZH | 1c | 50mm | 13 | 0.525 | Trefoil | N/A | 104
| Cu/XLPE/LSZH | 1c | 70mm | 15.5 | 0.73 | Trefoil | N/A | 124
| Cu/XLPE/LSZH | 1c | 95mm | 18 | 0.99 | Trefoil | N/A | 144
| Cu/XLPE/LSZH | 1c | 120mm | 19.5 | 1.23 | Trefoil | 60 | 156
| Cu/XLPE/LSZH | 1c | 150mm | 32 | 2.15 | Trefoil | 79 | 256
| Cu/XLPE/LSZH | 1c | 185mm | 32 | 2.4 | Trefoil | 79 | 256
| Cu/XLPE/LSZH | 1c | 240mm | 40 | 2.7 | Trefoil | 105 | 320
| Cu/XLPE/LSZH | 1c | 300mm | 40 | 2.95 | Trefoil | 105 | 320
| Cu/XLPE/LSZH | 1c | 400mm | 50 | 3.3 | Trefoil | 121 | 400
| Cu/XLPE/LSZH | 1c | 500mm | 50 | 3.75 | Trefoil | 121 | 400
| Cu/XLPE/LSZH | 1c | 630mm | 50 | 4.2 | Trefoil | 121 | 400
| Cu/XLPE/LSZH | 1c | 800mm | 63 | 4.75 | Trefoil | 152 | 504
| Cu/XLPE/LSZH | 1c | 1000mm | 63 | 5.3 | Trefoil | 152 | 504
| Cu/XLPE/LSZH | 1c | 50mm | 13 | 0.525 | Quadcleat | N/A | 104
| Cu/XLPE/LSZH | 1c | 70mm | 15.5 | 0.73 | Quadcleat | N/A | 124
| Cu/XLPE/LSZH | 1c | 95mm | 18 | 0.99 | Quadcleat | N/A | 144
| Cu/XLPE/LSZH | 1c | 120mm | 19.5 | 1.23 | Quadcleat | N/A | 156
| Cu/XLPE/LSZH | 1c | 150mm | 32 | 2.15 | Quadcleat | 90 | 256
| Cu/XLPE/LSZH | 1c | 185mm | 32 | 2.4 | Quadcleat | 90 | 256
| Cu/XLPE/LSZH | 1c | 240mm | 40 | 2.7 | Quadcleat | 103 | 320
| Cu/XLPE/LSZH | 1c | 300mm | 40 | 2.95 | Quadcleat | 103 | 320
| Cu/XLPE/LSZH | 1c | 400mm | 50 | 3.3 | Quadcleat | 121 | 400
| Cu/XLPE/LSZH | 1c | 500mm | 50 | 3.75 | Quadcleat | 121 | 400
| Cu/XLPE/LSZH | 1c | 630mm | 50 | 4.2 | Quadcleat | 121 | 400
| Cu/XLPE/LSZH | 1c | 800mm | 63 | 4.75 | Quadcleat | 150 | 504
| Cu/XLPE/LSZH | 1c | 1000mm | 63 | 5.3 | Quadcleat | 150 | 504
BS 7846 F2 Fire Resistant Armoured FP400 (0.6/1kV) | FP400 | 2c | 1.5mm | 12.9 | 0.31 | Single |  | 103.2
| FP400 | 2c | 2.5mm | 14.1 | 0.38 | Single |  | 112.8
| FP400 | 2c | 4mm | 15.2 | 0.45 | Single |  | 121.6
| FP400 | 2c | 6mm | 16.4 | 0.53 | Single |  | 131.2
| FP400 | 2c | 10mm | 18.6 | 0.63 | Single |  | 148.8
| FP400 | 2c | 16mm | 21.4 | 0.92 | Single |  | 171.2
| FP400 | 2c | 25mm | 23.7 | 1.2 | Single |  | 189.6
| FP400 | 2c | 35mm | 27.2 | 1.6 | Single |  | 217.6
| FP400 | 2c | 50mm | 28 | 2 | Single |  | 224
| FP400 | 2c | 70mm | 30.7 | 2.4 | Single | 60 | 245.6
| FP400 | 2c | 95mm | 35.3 | 3.3 | Single | 60 | 282.4
| FP400 | 2c | 120mm | 36.6 | 3.8 | Single | 60 | 292.8
| FP400 | 2c | 150mm | 39.3 | 4.4 | Single | 63 | 314.4
| FP400 | 2c | 185mm | 44.2 | 5.7 | Single | 72 | 353.6
| FP400 | 2c | 240mm | 48 | 7.2 | Single | 72 | 384
| FP400 | 2c | 300mm | 51.8 | 8.3 | Single | 79 | 414.4
| FP400 | 2c | 400mm | 55.9 | 10.5 | Single | 85 | 447.2
| FP400 | 3c | 1.5mm | 13.4 | 0.34 | Single |  | 80.4
| FP400 | 3c | 2.5mm | 14.8 | 0.43 | Single |  | 88.8
| FP400 | 3c | 4mm | 16.1 | 0.51 | Single |  | 96.6
| FP400 | 3c | 6mm | 17.4 | 0.62 | Single |  | 104.4
| FP400 | 3c | 10mm | 20.3 | 0.93 | Single |  | 121.8
| FP400 | 3c | 16mm | 22.8 | 1.21 | Single |  | 136.8
| FP400 | 3c | 25mm | 27.4 | 1.8 | Single |  | 219.2
| FP400 | 3c | 35mm | 29.2 | 2.1 | Single |  | 233.6
| FP400 | 3c | 50mm | 33 | 2.6 | Single | 60 | 264
| FP400 | 3c | 70mm | 37 | 3.4 | Single | 60 | 296
| FP400 | 3c | 95mm | 40.6 | 4.5 | Single | 63 | 324.8
| FP400 | 3c | 120mm | 43.8 | 5.5 | Single | 72 | 350.4
| FP400 | 3c | 150mm | 48 | 6.9 | Single | 72 | 384
| FP400 | 3c | 185mm | 52 | 8.2 | Single | 79 | 416
| FP400 | 3c | 240mm | 57.1 | 10.2 | Single | 85 | 456.8
| FP400 | 3c | 300mm | 63 | 12.2 | Single | 105 | 504
| FP400 | 3c | 400mm | 69.5 | 15 | Single | 105 | 556
| FP400 | 4c | 1.5mm | 14.3 | 0.39 | Single |  | 114.4
| FP400 | 4c | 2.5mm | 16 | 0.49 | Single |  | 128
| FP400 | 4c | 4mm | 17.3 | 0.59 | Single |  | 138.4
| FP400 | 4c | 6mm | 19.6 | 0.83 | Single |  | 156.8
| FP400 | 4c | 10mm | 21.8 | 1.04 | Single |  | 174.4
| FP400 | 4c | 16mm | 24.6 | 1.37 | Single |  | 196.8
| FP400 | 4c | 25mm | 29.1 | 2.1 | Single |  | 232.8
| FP400 | 4c | 35mm | 32.2 | 2.5 | Single | 60 | 257.6
| FP400 | 4c | 50mm | 35 | 3.2 | Single | 60 | 280
| FP400 | 4c | 70mm | 40.2 | 4.5 | Single | 63 | 321.6
| FP400 | 4c | 95mm | 44 | 56 | Single | 72 | 352
| FP400 | 4c | 120mm | 48.4 | 7.2 | Single | 72 | 387.2
| FP400 | 4c | 150mm | 52.5 | 8.5 | Single | 79 | 420
| FP400 | 4c | 185mm | 57.1 | 10.3 | Single | 85 | 456.8
| FP400 | 4c | 240mm | 62.7 | 12.8 | Single | 96 | 501.6
| FP400 | 4c | 300mm | 69.6 | 15.6 | Single | 105 | 556.8
| FP400 | 4c | 400mm | 78 | 20.4 | Single | 112 | 624
| FP400 | 7c | 1.5mm | 16.4 | 0.5 | Single |  | 131.2
| FP400 | 7c | 2.5mm | 18.3 | 0.64 | Single |  | 146.4
| FP400 | 7c | 4mm | 20.8 | 0.91 | Single |  | 166.4
| FP400 | 12c | 1.5mm | 21.2 | 0.85 | Single |  | 169.6
| FP400 | 12c | 2.5mm | 24 | 1.09 | Single |  | 192
| FP400 | 12c | 4mm | 27.3 | 1.55 | Single |  | 218.4
| FP400 | 19c | 1.5mm | 24.2 | 1.12 | Single |  | 193.6
| FP400 | 19c | 2.5mm | 28.6 | 1.65 | Single |  | 228.8
| FP400 | 27c | 1.5mm | 29.4 | 1.65 | Single |  | 235.2
| FP400 | 27c | 2.5mm | 33.4 | 2.15 | Single | 60 | 267.2
| FP400 | 37c | 1.5mm | 32.2 | 2 | Single | 60 | 257.6
| FP400 | 37c | 2.5mm | 36.7 | 2.65 | Single | 60 | 293.6
BS 7846 F120 Fire Resistant Armoured Cable FP600S (0.6/1kV) | FP600S | 2c | 4mm | 20.3 | 0.8 | Single |  | 121.8
| FP600S | 2c | 6mm | 20.2 | 0.85 | Single |  | 121.2
| FP600S | 2c | 10mm | 22.9 | 1.1 | Single |  | 137.4
| FP600S | 2c | 16mm | 24.2 | 1.2 | Single |  | 145.2
| FP600S | 2c | 25mm | 26.7 | 1.55 | Single |  | 213.6
| FP600S | 2c | 35mm | 30.3 | 2.1 | Single | 60 | 242.4
| FP600S | 2c | 50mm | 30 | 2.1 | Single | 60 | 240
| FP600S | 2c | 70mm | 32.8 | 2.6 | Single | 60 | 262.4
| FP600S | 2c | 95mm | 35.2 | 3.4 | Single | 60 | 281.6
| FP600S | 2c | 120mm | 38.7 | 4.1 | Single | 63 | 309.6
| FP600S | 2c | 150mm | 41.5 | 4.8 | Single | 63 | 332
| FP600S | 2c | 185mm | 46.3 | 6.1 | Single | 72 | 370.4
| FP600S | 2c | 240mm | 50.9 | 7.5 | Single | 79 | 407.2
| FP600S | 2c | 300mm | 55.3 | 9 | Single | 85 | 442.4
| FP600S | 2c | 400mm | 60.5 | 10.9 | Single | 96 | 484
| FP600S | 3c | 4mm | 21.1 | 0.91 | Single |  | 168.8
| FP600S | 3c | 6mm | 20.4 | 0.85 | Single |  | 163.2
| FP600S | 3c | 10mm | 24.4 | 1.2 | Single |  | 195.2
| FP600S | 3c | 16mm | 25.6 | 1.4 | Single |  | 204.8
| FP600S | 3c | 25mm | 29.5 | 2 | Single |  | 236
| FP600S | 3c | 35mm | 32.3 | 2.45 | Single | 60 | 258.4
| FP600S | 3c | 50mm | 32.2 | 2.65 | Single | 60 | 257.6
| FP600S | 3c | 70mm | 35.2 | 3.35 | Single | 60 | 281.6
| FP600S | 3c | 95mm | 40.1 | 4.6 | Single | 63 | 320.8
| FP600S | 3c | 120mm | 43.4 | 5.45 | Single | 72 | 347.2
| FP600S | 3c | 150mm | 48.5 | 6.95 | Single | 72 | 388
| FP600S | 3c | 185mm | 52.4 | 8.25 | Single | 79 | 419.2
| FP600S | 3c | 240mm | 57.5 | 10.3 | Single | 85 | 460
| FP600S | 3c | 300mm | 62.6 | 12.35 | Single | 96 | 500.8
| FP600S | 3c | 400mm | 68.8 | 15.2 | Single | 105 | 550.4
| FP600S | 4c | 4mm | 20.8 | 0.86 | Single |  | 166.4
| FP600S | 4c | 6mm | 22.1 | 1 | Single |  | 176.8
| FP600S | 4c | 10mm | 26 | 1.4 | Single |  | 208
| FP600S | 4c | 16mm | 27.8 | 1.65 | Single |  | 222.4
| FP600S | 4c | 25mm | 32.1 | 2.35 | Single | 60 | 256.8
| FP600S | 4c | 35mm | 35.3 | 2.95 | Single | 60 | 282.4
| FP600S | 4c | 50mm | 36.4 | 3.3 | Single | 60 | 291.2
| FP600S | 4c | 70mm | 40.5 | 4.55 | Single | 63 | 324
| FP600S | 4c | 95mm | 44.3 | 5.7 | Single | 72 | 354.4
| FP600S | 4c | 120mm | 49.4 | 7.35 | Single | 79 | 395.2
| FP600S | 4c | 150mm | 58.8 | 8.7 | Single | 96 | 470.4
| FP600S | 4c | 185mm | 53.6 | 10.5 | Single | 79 | 428.8
| FP600S | 4c | 240mm | 64.4 | 13.1 | Single | 105 | 515.2
| FP600S | 4c | 300mm | 69.9 | 15.75 | Single | 105 | 559.2
| FP600S | 4c | 400mm | 78.6 | 20.35 | Single | 112 | 628.8
| FP600S | 5c | 4mm | 23 | 1.05 | Single |  | 184
| FP600S | 5c | 6mm | 23.7 | 1.15 | Single |  | 189.6
| FP600S | 5c | 10mm | 28.8 | 1.65 | Single |  | 230.4
| FP600S | 5c | 16mm | 31.3 | 2.1 | Single | 60 | 250.4
| FP600S | 5c | 25mm | 34.7 | 2.75 | Single | 60 | 277.6
| FP600S | 5c | 35mm | 38.2 | 3.35 | Single | 60 | 305.6
H07ZZ-F BS EN 50525-3-21 Cu/LSZH/LSZH Rubber Flexible Cable (0.45/0.75kV) | Cu/LSZH/LSZH | 1c | 1.5mm | 6.4 | 0.063 | Single |  | 51.2
| Cu/LSZH/LSZH | 1c | 2.5mm | 7.1 | 0.076 | Single |  | 56.8
| Cu/LSZH/LSZH | 1c | 4mm | 8.1 | 0.107 | Single |  | 64.8
| Cu/LSZH/LSZH | 1c | 6mm | 8.85 | 0.14 | Single |  | 70.8
| Cu/LSZH/LSZH | 1c | 10mm | 10.7 | 0.213 | Single |  | 85.6
| Cu/LSZH/LSZH | 1c | 16mm | 12.1 | 0.291 | Single |  | 96.8
| Cu/LSZH/LSZH | 1c | 25mm | 14.25 | 0.415 | Single |  | 114
| Cu/LSZH/LSZH | 1c | 35mm | 16.1 | 0.539 | Single |  | 128.8
| Cu/LSZH/LSZH | 1c | 50mm | 18.55 | 0.74 | Single |  | 148.4
| Cu/LSZH/LSZH | 1c | 70mm | 20.95 | 0.989 | Single |  | 167.6
| Cu/LSZH/LSZH | 1c | 95mm | 23.4 | 1.29 | Single |  | 187.2
| Cu/LSZH/LSZH | 1c | 120mm | 25.7 | 1.592 | Single |  | 205.6
| Cu/LSZH/LSZH | 1c | 150mm | 28.3 | 1.957 | Single |  | 226.4
| Cu/LSZH/LSZH | 1c | 185mm | 31 | 2.35 | Single | 60 | 248
| Cu/LSZH/LSZH | 1c | 240mm | 34.45 | 3.099 | Single | 60 | 275.6
| Cu/LSZH/LSZH | 1c | 300mm | 37.7 | 3.687 | Single | 60 | 301.6
| Cu/LSZH/LSZH | 1c | 400mm | 42.1 | 4.85 | Single | 63 | 336.8
| Cu/LSZH/LSZH | 1c | 500mm | 46.65 | 5.998 | Single | 72 | 373.2
| Cu/LSZH/LSZH | 1c | 1.5mm | 6.4 | 0.063 | Trefoil | N/A | 51.2
| Cu/LSZH/LSZH | 1c | 2.5mm | 7.1 | 0.076 | Trefoil | N/A | 56.8
| Cu/LSZH/LSZH | 1c | 4mm | 8.1 | 0.107 | Trefoil | N/A | 64.8
| Cu/LSZH/LSZH | 1c | 6mm | 8.85 | 0.14 | Trefoil | N/A | 70.8
| Cu/LSZH/LSZH | 1c | 10mm | 10.7 | 0.213 | Trefoil | N/A | 85.6
| Cu/LSZH/LSZH | 1c | 16mm | 12.1 | 0.291 | Trefoil | N/A | 96.8
| Cu/LSZH/LSZH | 1c | 25mm | 14.25 | 0.415 | Trefoil | N/A | 114
| Cu/LSZH/LSZH | 1c | 35mm | 16.1 | 0.539 | Trefoil | N/A | 128.8
| Cu/LSZH/LSZH | 1c | 50mm | 18.55 | 0.74 | Trefoil | N/A | 148.4
| Cu/LSZH/LSZH | 1c | 70mm | 20.95 | 0.989 | Trefoil | 60 | 167.6
| Cu/LSZH/LSZH | 1c | 95mm | 23.4 | 1.29 | Trefoil | 63 | 187.2
| Cu/LSZH/LSZH | 1c | 120mm | 25.7 | 1.592 | Trefoil | 63 | 205.6
| Cu/LSZH/LSZH | 1c | 150mm | 28.3 | 1.957 | Trefoil | 72 | 226.4
| Cu/LSZH/LSZH | 1c | 185mm | 31 | 2.35 | Trefoil | 79 | 248
| Cu/LSZH/LSZH | 1c | 240mm | 34.45 | 3.099 | Trefoil | 85 | 275.6
| Cu/LSZH/LSZH | 1c | 300mm | 37.7 | 3.687 | Trefoil | 96 | 301.6
| Cu/LSZH/LSZH | 1c | 400mm | 42.1 | 4.85 | Trefoil | 105 | 336.8
| Cu/LSZH/LSZH | 1c | 500mm | 46.65 | 5.998 | Trefoil | 121 | 373.2
| Cu/LSZH/LSZH | 1c | 1.5mm | 6.4 | 0.063 | Quadcleat | N/A | 51.2
| Cu/LSZH/LSZH | 1c | 2.5mm | 7.1 | 0.076 | Quadcleat | N/A | 56.8
| Cu/LSZH/LSZH | 1c | 4mm | 8.1 | 0.107 | Quadcleat | N/A | 64.8
| Cu/LSZH/LSZH | 1c | 6mm | 8.85 | 0.14 | Quadcleat | N/A | 70.8
| Cu/LSZH/LSZH | 1c | 10mm | 10.7 | 0.213 | Quadcleat | N/A | 85.6
| Cu/LSZH/LSZH | 1c | 16mm | 12.1 | 0.291 | Quadcleat | N/A | 96.8
| Cu/LSZH/LSZH | 1c | 25mm | 14.25 | 0.415 | Quadcleat | N/A | 114
| Cu/LSZH/LSZH | 1c | 35mm | 16.1 | 0.539 | Quadcleat | N/A | 128.8
| Cu/LSZH/LSZH | 1c | 50mm | 18.55 | 0.74 | Quadcleat | N/A | 148.4
| Cu/LSZH/LSZH | 1c | 70mm | 20.95 | 0.989 | Quadcleat | N/A | 167.6
| Cu/LSZH/LSZH | 1c | 95mm | 23.4 | 1.29 | Quadcleat | 68 | 187.2
| Cu/LSZH/LSZH | 1c | 120mm | 25.7 | 1.592 | Quadcleat | 70 | 205.6
| Cu/LSZH/LSZH | 1c | 150mm | 28.3 | 1.957 | Quadcleat | 78 | 226.4
| Cu/LSZH/LSZH | 1c | 185mm | 31 | 2.35 | Quadcleat | 90 | 248
| Cu/LSZH/LSZH | 1c | 240mm | 34.45 | 3.099 | Quadcleat | 90 | 275.6
| Cu/LSZH/LSZH | 1c | 300mm | 37.7 | 3.687 | Quadcleat | 103 | 301.6
| Cu/LSZH/LSZH | 1c | 400mm | 42.1 | 4.85 | Quadcleat | 120 | 336.8
| Cu/LSZH/LSZH | 1c | 500mm | 46.65 | 5.998 | Quadcleat | 120 | 373.2
N2XH Enhanced Flex FRNC-LSZH KEMA | N2XH Enhanced Flex | 1c | 1.5mm | 5.4 | 0.066 | Single | N/A | 43.2
| N2XH Enhanced Flex | 1c | 2.5mm | 5.8 | 0.077 | Single | N/A | 46.4
| N2XH Enhanced Flex | 1c | 4mm | 6.3 | 0.074 | Single | N/A | 50.4
| N2XH Enhanced Flex | 1c | 6mm | 6.8 | 0.095 | Single | N/A | 54.4
| N2XH Enhanced Flex | 1c | 10mm | 7.9 | 0.138 | Single | N/A | 63.2
| N2XH Enhanced Flex | 1c | 16mm | 9.1 | 0.199 | Single | N/A | 72.8
| N2XH Enhanced Flex | 1c | 25mm | 10.8 | 0.288 | Single | N/A | 86.4
| N2XH Enhanced Flex | 1c | 35mm | 11.7 | 0.381 | Single | N/A | 93.6
| N2XH Enhanced Flex | 1c | 50mm | 13.7 | 0.526 | Single | N/A | 109.6
| N2XH Enhanced Flex | 1c | 70mm | 15.8 | 0.72 | Single | N/A | 126.4
| N2XH Enhanced Flex | 1c | 95mm | 17.3 | 0.941 | Single | N/A | 138.4
| N2XH Enhanced Flex | 1c | 120mm | 19 | 1.183 | Single | N/A | 152
| N2XH Enhanced Flex | 1c | 150mm | 21.4 | 1.456 | Single | N/A | 171.2
| N2XH Enhanced Flex | 1c | 185mm | 24.2 | 1.807 | Single | N/A | 193.6
| N2XH Enhanced Flex | 1c | 240mm | 26.4 | 2.295 | Single | N/A | 211.2
| N2XH Enhanced Flex | 1c | 300mm | 29.7 | 2.846 | Single | N/A | 237.6
| N2XH Enhanced Flex | 1c | 400mm | 33.4 | 3.681 | Single | 60 | 267.2
| N2XH Enhanced Flex | 1c | 500mm | 37.3 | 4.72 | Single | 60 | 298.4
| N2XH Enhanced Flex | 1c | 630mm | 41.2 | 6.176 | Single | 60 | 329.6
| N2XH Enhanced Flex | 2c | 1.5mm | 10 | 0.147 | Single | N/A | 80
| N2XH Enhanced Flex | 2c | 2.5mm | 10.8 | 0.179 | Single | N/A | 86.4
| N2XH Enhanced Flex | 2c | 4mm | 11.8 | 0.226 | Single | N/A | 94.4
| N2XH Enhanced Flex | 2c | 6mm | 12.8 | 0.281 | Single | N/A | 102.4
| N2XH Enhanced Flex | 2c | 10mm | 15.2 | 0.412 | Single | N/A | 121.6
| N2XH Enhanced Flex | 2c | 16mm | 17.5 | 0.577 | Single | N/A | 140
| N2XH Enhanced Flex | 2c | 25mm | 21.4 | 0.858 | Single | N/A | 171.2
| N2XH Enhanced Flex | 2c | 35mm | 23.2 | 1.092 | Single | N/A | 185.6
| N2XH Enhanced Flex | 2c | 50mm | 27.1 | 1.503 | Single | N/A | 216.8
| N2XH Enhanced Flex | 2c | 70mm | 31.6 | 2.045 | Single | 60 | 252.8
| N2XH Enhanced Flex | 2c | 95mm | 34.8 | 2.643 | Single | 60 | 278.4
| N2XH Enhanced Flex | 2c | 120mm | 38.6 | 3.318 | Single | 60 | 308.8
| N2XH Enhanced Flex | 2c | 150mm | 43.7 | 4.146 | Single | 63 | 349.6
| N2XH Enhanced Flex | 2c | 185mm | 49.8 | 5.215 | Single | 63 | 398.4
| N2XH Enhanced Flex | 2c | 240mm | 54.2 | 6.491 | Single | 72 | 433.6
| N2XH Enhanced Flex | 2c | 300mm | 60.8 | 8.079 | Single | 72 | 486.4
| N2XH Enhanced Flex | 2c | 400mm | 67.6 | 10.39 | Single | 85 | 540.8
| N2XH Enhanced Flex | 3c | 1.5mm | 10.5 | 0.165 | Single | N/A | 84
| N2XH Enhanced Flex | 3c | 2.5mm | 11.3 | 0.206 | Single | N/A | 90.4
| N2XH Enhanced Flex | 3c | 4mm | 12.4 | 0.266 | Single | N/A | 99.2
| N2XH Enhanced Flex | 3c | 6mm | 13.5 | 0.337 | Single | N/A | 108
| N2XH Enhanced Flex | 3c | 10mm | 16.1 | 0.503 | Single | N/A | 128.8
| N2XH Enhanced Flex | 3c | 16mm | 18.6 | 0.718 | Single | N/A | 148.8
| N2XH Enhanced Flex | 3c | 25mm | 22.7 | 1.071 | Single | N/A | 181.6
| N2XH Enhanced Flex | 3c | 35mm | 24.7 | 1.388 | Single | N/A | 197.6
| N2XH Enhanced Flex | 3c | 50mm | 29.1 | 1.919 | Single | N/A | 232.8
| N2XH Enhanced Flex | 3c | 70mm | 34 | 2.603 | Single | 60 | 272
| N2XH Enhanced Flex | 3c | 95mm | 37.2 | 3.423 | Single | 60 | 297.6
| N2XH Enhanced Flex | 3c | 120mm | 41.2 | 4.316 | Single | 60 | 329.6
| N2XH Enhanced Flex | 3c | 150mm | 46.9 | 5.397 | Single | 63 | 375.2
| N2XH Enhanced Flex | 3c | 185mm | 53.4 | 6.761 | Single | 72 | 427.2
| N2XH Enhanced Flex | 3c | 240mm | 57.9 | 8.483 | Single | 72 | 463.2
| N2XH Enhanced Flex | 3c | 300mm | 65.3 | 10.583 | Single | 85 | 522.4
| N2XH Enhanced Flex | 3c | 400mm | 73.2 | 13.671 | Single | 85 | 585.6
| N2XH Enhanced Flex | 4c | 1.5mm | 11.3 | 0.193 | Single | N/A | 90.4
| N2XH Enhanced Flex | 4c | 2.5mm | 12.2 | 0.243 | Single | N/A | 97.6
| N2XH Enhanced Flex | 4c | 4mm | 13.4 | 0.32 | Single | N/A | 107.2
| N2XH Enhanced Flex | 4c | 6mm | 14.6 | 0.411 | Single | N/A | 116.8
| N2XH Enhanced Flex | 4c | 10mm | 17.5 | 0.62 | Single | N/A | 140
| N2XH Enhanced Flex | 4c | 16mm | 20.3 | 0.895 | Single | N/A | 162.4
| N2XH Enhanced Flex | 4c | 25mm | 24.9 | 1.34 | Single | N/A | 199.2
| N2XH Enhanced Flex | 4c | 35mm | 27.3 | 1.752 | Single | N/A | 218.4
| N2XH Enhanced Flex | 4c | 50mm | 32 | 2.449 | Single | 60 | 256
| N2XH Enhanced Flex | 4c | 70mm | 37.4 | 3.379 | Single | 60 | 299.2
| N2XH Enhanced Flex | 4c | 95mm | 41.2 | 4.387 | Single | 60 | 329.6
| N2XH Enhanced Flex | 4c | 120mm | 45.9 | 5.561 | Single | 63 | 367.2
| N2XH Enhanced Flex | 4c | 150mm | 51.9 | 7.091 | Single | 72 | 415.2
| N2XH Enhanced Flex | 4c | 185mm | 59.2 | 8.691 | Single | 79 | 473.6
| N2XH Enhanced Flex | 4c | 240mm | 64.4 | 10.919 | Single | 85 | 515.2
| N2XH Enhanced Flex | 4c | 300mm | 72.6 | 13.618 | Single | 96 | 580.8
| N2XH Enhanced Flex | 4c | 400mm | 80.8 | 17.511 | Single | 105 | 646.4
| N2XH Enhanced Flex | 1c | 1.5mm | 5.4 | 0.066 | Trefoil | N/A | 43.2
| N2XH Enhanced Flex | 1c | 2.5mm | 5.8 | 0.077 | Trefoil | N/A | 46.4
| N2XH Enhanced Flex | 1c | 4mm | 6.3 | 0.074 | Trefoil | N/A | 50.4
| N2XH Enhanced Flex | 1c | 6mm | 6.8 | 0.095 | Trefoil | N/A | 54.4
| N2XH Enhanced Flex | 1c | 10mm | 7.9 | 0.138 | Trefoil | N/A | 63.2
| N2XH Enhanced Flex | 1c | 16mm | 9.1 | 0.199 | Trefoil | N/A | 72.8
| N2XH Enhanced Flex | 1c | 25mm | 10.8 | 0.288 | Trefoil | N/A | 86.4
| N2XH Enhanced Flex | 1c | 35mm | 11.7 | 0.381 | Trefoil | N/A | 93.6
| N2XH Enhanced Flex | 1c | 50mm | 13.7 | 0.526 | Trefoil | N/A | 109.6
| N2XH Enhanced Flex | 1c | 70mm | 15.8 | 0.72 | Trefoil | N/A | 126.4
| N2XH Enhanced Flex | 1c | 95mm | 17.3 | 0.941 | Trefoil | N/A | 138.4
| N2XH Enhanced Flex | 1c | 120mm | 19 | 1.183 | Trefoil | 60 | 152
| N2XH Enhanced Flex | 1c | 150mm | 21.4 | 1.456 | Trefoil | 60 | 171.2
| N2XH Enhanced Flex | 1c | 185mm | 24.2 | 1.807 | Trefoil | 63 | 193.6
| N2XH Enhanced Flex | 1c | 240mm | 26.4 | 2.295 | Trefoil | 63 | 211.2
| N2XH Enhanced Flex | 1c | 300mm | 29.7 | 2.846 | Trefoil | 72 | 237.6
| N2XH Enhanced Flex | 1c | 400mm | 33.4 | 3.681 | Trefoil | 79 | 267.2
| N2XH Enhanced Flex | 1c | 500mm | 37.3 | 4.72 | Trefoil | 85 | 298.4
| N2XH Enhanced Flex | 1c | 630mm | 41.2 | 6.176 | Trefoil | 96 | 329.6
| N2XH Enhanced Flex | 1c | 1.5mm | 5.4 | 0.066 | Quadcleat | N/A | 43.2
| N2XH Enhanced Flex | 1c | 2.5mm | 5.8 | 0.077 | Quadcleat | N/A | 46.4
| N2XH Enhanced Flex | 1c | 4mm | 6.3 | 0.074 | Quadcleat | N/A | 50.4
| N2XH Enhanced Flex | 1c | 6mm | 6.8 | 0.095 | Quadcleat | N/A | 54.4
| N2XH Enhanced Flex | 1c | 10mm | 7.9 | 0.138 | Quadcleat | N/A | 63.2
| N2XH Enhanced Flex | 1c | 16mm | 9.1 | 0.199 | Quadcleat | N/A | 72.8
| N2XH Enhanced Flex | 1c | 25mm | 10.8 | 0.288 | Quadcleat | N/A | 86.4
| N2XH Enhanced Flex | 1c | 35mm | 11.7 | 0.381 | Quadcleat | N/A | 93.6
| N2XH Enhanced Flex | 1c | 50mm | 13.7 | 0.526 | Quadcleat | N/A | 109.6
| N2XH Enhanced Flex | 1c | 70mm | 15.8 | 0.72 | Quadcleat | N/A | 126.4
| N2XH Enhanced Flex | 1c | 95mm | 17.3 | 0.941 | Quadcleat | N/A | 138.4
| N2XH Enhanced Flex | 1c | 120mm | 19 | 1.183 | Quadcleat | N/A | 152
| N2XH Enhanced Flex | 1c | 150mm | 21.4 | 1.456 | Quadcleat | N/A | 171.2
| N2XH Enhanced Flex | 1c | 185mm | 24.2 | 1.807 | Quadcleat | 68 | 193.6
| N2XH Enhanced Flex | 1c | 240mm | 26.4 | 2.295 | Quadcleat | 70 | 211.2
| N2XH Enhanced Flex | 1c | 300mm | 29.7 | 2.846 | Quadcleat | 78 | 237.6
| N2XH Enhanced Flex | 1c | 400mm | 33.4 | 3.681 | Quadcleat | 90 | 267.2
| N2XH Enhanced Flex | 1c | 500mm | 37.3 | 4.72 | Quadcleat | 103 | 298.4
| N2XH Enhanced Flex | 1c | 630mm | 41.2 | 6.176 | Quadcleat | 103 | 329.6