## Cover Sheet
ODN56 Data Centre
Cassin Networks ApS
LV CABLES - ODN6 NETWORK CORE SCHEDULE
LV CABLES - ODN5 NETWORK CORE SCHEDULE
Job No: | 1029161
Doc No: | ODN56-E-SCH-0003
Document Revision History | [6 empty] | Schedules Inclusive
Revision Ref | Issue Date |  | Stage/ Purpose of issue/ Description of revision |  |  |  | Reference
0 | 2021-09-15 |  | ISSUE FOR CONSTRUCTION (IFC)
1 | 2022-02-02 |  | ISSUE FOR ADDENDUM 1
Document Validation (latest issue)
Revision Ref | Issue Date | Purpose of Issue | Stage/ Purpose of issue/ Description of revision
1 | 2022-02-02 | ISSUE FOR ADDENDUM 1 |  | Prepared by | Checked by | Approved by
|  |  | Initials | BP | JPr | JP

## Cable_Schedule_ODN5
Schedule Name |  |  |  | Client | [6 empty] | Status
LV CABLES - ODN6 NETWORK CORE SCHEDULE |  |  |  | Cassin Network ApS | [6 empty] | ISSUE FOR ADDENDUM 1
Schedule Number
ODN56-E-SCH-0003
Project Name
Revision | Date |  |  | ODN56 Data Centre | [6 empty] | Prepared | Checked | Verified
1 | 2022-02-02 | [9 empty] | BP | JPr | JP
Notes: LVSV = Low Voltage Switchgear Vendor, EC = Electrical Contractor MVSV = Medium Voltage Switchgear Vendor, GV = Generator Vendor, HPB = High Power Bar Vendor Multicore Spacing (1 x OD), Single Core Quad./Trefoil (2 x OD)
LV CABLES - ODN5 NETWORK CORE SCHEDULE
Cable Information
Cable ID | Cable Routes |  | Cable Configuration | Cable Size (mm²) | Cable Type | No of CPCs | CPC Type | CPC Size (mm²) | Protective Device |  |  |  |  | Installation Method | Supplied and Installed By
| From | To | [6 empty] | Type | Poles | Frame Rating (A) | Device Rating (A) | Overload setting (A)
PTX-N1-01 | PTX-N1-01 | MSB-N1 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
PTX-N1-02 | PTX-N1-02 | MSB-N1 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
EG-N1-01 | EG-N1 | MSB-N1 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
MSB-N1-01 | MSB-N1 | UPS-N1A | 3 x 3 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | MCCB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N1-02 | MSB-N1 | UPS-N1B | 3 x 3 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | MCCB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N1-03 | MSB-N1 | STC-N1 | 6 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 500 | MCCB | 3P | 4000 | 4000 | 3600 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N1-04 | MSB-N1 | HMD-N1 | 3 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 240 | MCCB | 3P&N | 1250 | 1250 | 1250 | Cable Ladder (External/ Internal) - Quad/Trefoil | LVSV
MSB-N1-05 | MSB-N1 | L-R-1R/N1 | 3 x 4 x 1c | 240 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 240 | MCCB | 3P&N | 1000 | 1000 | 1000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N1-01/01 | UPS-N1A | STC-N1 | 3 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | ACB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N1-02/01 | UPS-N1B | STC-N1 | 3 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | ACB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
STC-N1-01 | STC-N1 | PDU-N1-1 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N1-02 | STC-N1 | PDU-N1-2 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N1-03 | STC-N1 | PDU-N1-3 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N1-04 | STC-N1 | PDU-N1-4 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N1-05 | STC-N1 | PDU-N1-5 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N1-06 | STC-N1 | PDU-N1-6 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N1-07 | STC-N1 | PDU-N1-7 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N1-08 | STC-N1 | PDU-N1-8 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
PDU-N1-1-1 | PDU-N1-1 | RB-GS1.MDF2-01-01A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-1-2 | PDU-N1-1 | RB-MPOE1-02-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-1-3 | PDU-N1-1 | RB-MDFA-02F-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-1-4 | PDU-N1-1 | RB-MDFB-02F-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-2-1 | PDU-N1-2 | RB-MPOE2-03-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-2-2 | PDU-N1-2 | RB-MPOE2-03-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-2-3 | PDU-N1-2 | RB-MDFD-02B-1A | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-2-4 | PDU-N1-2 | RB-MDFA-02F-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-3-1 | PDU-N1-3 | RB-MPOE1-03-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-3-2 | PDU-N1-3 | RB-BDF1-02-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-3-3 | PDU-N1-3 | RB-BDF1-03-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-3-4 | PDU-N1-3 | RB-MDFA-01B-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-3-5 | PDU-N1-3 | RB-MDFB-01B-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-4-1 | PDU-N1-4 | RB-GS2.MDF2-02-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-4-2 | PDU-N1-4 | RB-GS2.MDF1-01-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-4-3 | PDU-N1-4 | RB-BDF1-03-3A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-4-4 | PDU-N1-4 | RB-MDFB-01F-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-4-5 | PDU-N1-4 | RB-MDFC-01F-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-5-1 | PDU-N1-5 | RB-BDF1-02-4A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-5-2 | PDU-N1-5 | RB-BDF2-03-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-5-3 | PDU-N1-5 | RB-MDFA-02B-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-5-4 | PDU-N1-5 | RB-MDFC-01B-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-6-1 | PDU-N1-6 | RB-MDFB-01B-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-6-2 | PDU-N1-6 | RB-MDFC-01B-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-6-3 | PDU-N1-6 | RB-MDFD-02F-2A | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-6-4 | PDU-N1-6 | RB-MDFC-02F-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-7-1 | PDU-N1-7 | RB-BDF2-02-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-7-2 | PDU-N1-7 | RB-BDF2-02-3B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-7-3 | PDU-N1-7 | RB-BDF2-03-3B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-7-4 | PDU-N1-7 | RB-MDFD-01B-1B | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-8-1 | PDU-N1-8 | DB-ESRA-UPS-A | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N1-8-2 | PDU-N1-8 | DB-ESRB-UPS-A | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N1-8-3 | PDU-N1-8 | DB-HMDA-UPS-A | 1 x 1 x 4c | 50 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N1-8-4 | PDU-N1-8 | DB-IDF-UPS-A | 1 x 1 x 4c | 185 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-8-5 | PDU-N1-8 | DB-HMDN1-UPS | 1 x 1 x 4c | 50 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
PDU-N1-8-6 | PDU-N1-8 | RB-MDFD-02F-1B | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-8-7 | PDU-N1-8 | DB-NSR1-UPS-A | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
HMD-N1-01 | HMD-N1 | HMD-MDFA-N1 | 1 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 120 | MCCB | 3P&N | 400 | 400 | 400 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
HMD-N1-02 | HMD-N1 | HMD-MDFC-N1 | 1 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 120 | MCCB | 3P&N | 400 | 400 | 400 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
HMD-N1-03 | HMD-N1 | MPOE1.AHU.01 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N1-04 | HMD-N1 | BDF1.AHU.02 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N1-05 | HMD-N1 | BDF1.AHU.01 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N1-06 | HMD-N1 | ERN1.AHU.01 | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N1-07 | HMD-N1 | ERN1.AHU.03 | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N1-08 | HMD-N1 | DB-HMDN1-LP | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 250 | 250 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N2-01 | HMD-MDFA-N2 | MDF A SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N2-02 | HMD-MDFA-N2 | MDF A RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N2-04 | HMD-MDFA-N2 | MDF A AHU CP | 1 x 1 x 2c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N2-05 | HMD-MDFA-N2 | ECH PUMP MDF A AHU1. ECH | 1 x 1 x 2c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 16 | 16 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N2-06 | HMD-MDFA-N2 | MDFA.RIOB.ICPNL | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 25 | 25 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N2-07 | HMD-MDFA-N2 | MDF B SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N2-08 | HMD-MDFA-N2 | MDF B RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N3-01 | HMD-MDFB-N3 | MDF B SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N3-02 | HMD-MDFB-N3 | MDF B RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N3-04 | HMD-MDFB-N3 | MDF B AHU CP | 1 x 1 x 2c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N3-05 | HMD-MDFB-N3 | ECH PUMP MDF B AHU2. ECH | 1 x 1 x 2c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 16 | 16 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N3-06 | HMD-MDFB-N2 | MDFA.RIOB.ICPNL | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 25 | 25 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N3-07 | HMD-MDFB-N3 | MDF A SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N3-08 | HMD-MDFB-N3 | MDF A RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
PTX-N2-01 | PTX-N2-01 | MSB-N2 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
PTX-N2-02 | PTX-N2-02 | MSB-N2 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
EG-N2-01 | EG-N2 | MSB-N2 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
MSB-N2-01 | MSB-N2 | UPS-N2A | 3 x 3 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | MCCB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N2-02 | MSB-N2 | UPS-N2B | 3 x 3 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | MCCB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N2-03 | MSB-N2 | STC-N2 | 6 x 3 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 500 | MCCB | 3P | 4000 | 4000 | 3600 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N2-04 | MSB-N2 | HMD-N2 | 3 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 240 | MCCB | 3P&N | 1250 | 1250 | 1250 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
MSB-N2-05 | MSB-N2 | L-R-2R/N2 | 2 x 4 x 1c | 240 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 240 | MCCB | 3P&N | 1000 | 1000 | 1000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N2-01/01 | UPS-N2A | STC-N2 | 3 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | ACB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N2-02/01 | UPS-N2B | STC-N2 | 3 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | ACB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
STC-N2-01 | STC-N2 | PDU-N2-1 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N2-02 | STC-N2 | PDU-N2-2 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N2-03 | STC-N2 | PDU-N2-3 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N2-04 | STC-N2 | PDU-N2-4 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N2-05 | STC-N2 | PDU-N2-5 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N2-06 | STC-N2 | PDU-N2-6 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N2-07 | STC-N2 | PDU-N2-7 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N2-08 | STC-N2 | PDU-N2-8 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
PDU-N2-1-1 | PDU-N2-1 | RB-GS1.MDF2-01-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-1-2 | PDU-N2-1 | RB-MPOE1-03-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-1-3 | PDU-N2-1 | RB-GS2.MDF2-02-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-1-4 | PDU-N2-1 | RB-BDF1-03-4B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-1-5 | PDU-N2-1 | RB-MDFD-01B-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-2-1 | PDU-N2-2 | RB-BDF2-02-4A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-2-2 | PDU-N2-2 | RB-MDFA-01F-2A | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-2-3 | PDU-N2-2 | RB-MPOE1-02-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-2-4 | PDU-N2-2 | RB-MPOE2-02-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-2-5 | PDU-N2-2 | RB-MDFB-01B-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-3-1 | PDU-N2-3 | RB-MDFB-02F-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-3-2 | PDU-N2-3 | RB-MDFB-02B-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-3-3 | PDU-N2-3 | RB-BDF2-02-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-3-4 | PDU-N2-3 | RB-MDFA-01F-1B | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-4-1 | PDU-N2-4 | RB-BDF2-03-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-4-2 | PDU-N2-4 | RB-MDFA-02B-2B | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-4-3 | PDU-N2-4 | RB-MDFC-01F-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-4-4 | PDU-N2-4 | RB-MDFC-02B-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-5-1 | PDU-N2-5 | RB-MPOE2-02-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-5-2 | PDU-N2-5 | RB-BDF1-02-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-5-3 | PDU-N2-5 | RB-BDF1-03-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-5-4 | PDU-N2-5 | RB-MDFB-02F-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-6-1 | PDU-N2-6 | RB-MDFA-01B-1A | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-6-2 | PDU-N2-6 | RB-MDFC-02F-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-6-3 | PDU-N2-6 | RB-MDFC-02B-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-7-1 | PDU-N2-7 | RB-BDF1-02-3A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-7-2 | PDU-N2-7 | RB-MDFD-01F-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-7-3 | PDU-N2-7 | RB-GS2.MDF1-01-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-7-4 | PDU-N2-7 | RB-BDF2-03-4B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-8-1 | PDU-N2-8 | RB-MDFD-01B-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-8-2 | PDU-N2-8 | DB-ESRC-UPS-A | 1 x 1 x 4c | 50 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N2-8-3 | PDU-N2-8 | DB-ESRD-UPS-A | 1 x 1 x 4c | 50 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N2-8-4 | PDU-N2-8 | DB-HMDC-UPS-A | 1 x 1 x 4c | 50 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
PDU-N2-8-5 | PDU-N2-8 | DB-IDF-UPS-B | 1 x 1 x 4c | 120 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-8-6 | PDU-N2-8 | ADM.VENT.EX.FAN6 | 1 x 1 x 4c | 50 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 40 | Cable Ladder (Internal) - Touching | EC
PDU-N2-8-7 | PDU-N2-8 | RB-MDFD-02F-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-8-8 | PDU-N2-8 | DB-NSR2-UPS-B | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 250 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
HMD-N2-01 | HMD-N2 | HMD-MDFA-N2 | 1 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 120 | MCCB | 3P&N | 400 | 400 | 400 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
HMD-N2-02 | HMD-N2 | HMD-MDFC-N2 | 1 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 120 | MCCB | 3P&N | 400 | 400 | 400 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
HMD-N2-03 | HMD-N2 | MPOE1.AHU.02 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N2-04 | HMD-N2 | BDF1 AHU.03 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N2-05 | HMD-N2 | BDF1.AHU.02 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N2-06 | HMD-N2 | ERN2.AHU.01 | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N2-07 | HMD-N2 | ERN2.AHU.03 | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N2-08 | HMD-N2 | DB-HMDN2-LP | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 250 | 250 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N1-01 | HMD-MDFA-N1 | MDF B SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N1-02 | HMD-MDFA-N1 | MDF B RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N1-04 | HMD-MDFA-N1 | MDF B AHU CP | 1 x 1 x 2c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N1-05 | HMD-MDFA-N1 | ECH PUMP MDF B AHU1. ECH | 1 x 1 x 2c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 16 | 16 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N1-06 | HMD-MDFA-N1 | MDFA.RIOA.ICPNL | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 25 | 25 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N1-07 | HMD-MDFA-N1 | MDF B SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N1-08 | HMD-MDFA-N1 | MDF B RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N4-01 | HMD-MDFB-N4 | MDF B SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N4-02 | HMD-MDFB-N4 | MDF B RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N4-04 | HMD-MDFB-N4 | MDF B AHU CP | 1 x 1 x 2c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N4-05 | HMD-MDFB-N4 | ECH PUMP MDF B AHU1. ECH | 1 x 1 x 2c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 16 | 16 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N4-06 | HMD-MDFB-N4 | MDFB.RIOA.ICPNL | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 25 | 25 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N4-07 | HMD-MDFB-N4 | MDF B SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N4-08 | HMD-MDFB-N4 | MDF B RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
PTX-N3-01 | PTX-N3-01 | MSB-N3 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
PTX-N3-02 | PTX-N3-02 | MSB-N3 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
EG-N3-01 | EG-N3 | MSB-N3 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
MSB-N3-01 | MSB-N3 | UPS-N3A | 3 x 3 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | MCCB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N3-02 | MSB-N3 | UPS-N3B | 3 x 3 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | MCCB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N3-03 | MSB-N3 | STC-N3 | 6 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 500 | MCCB | 3P | 4000 | 4000 | 3600 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N3-04 | MSB-N3 | HMD-N3 | 3 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 240 | MCCB | 3P&N | 1250 | 1250 | 1250 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
MSB-N3-05 | MSB-N3 | L-R-1R/N3 | 2x 4 x 1c | 240 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 240 | MCCB | 3P&N | 1000 | 1000 | 1000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N3-06 | MSB-N1 | SPRINKLER MCCP ADMIN | 3 x 1 x 4c | 150 | Enhanced fire resistant, insulated & sheathed - FP 600S | 1 | Separate | 240 | MCCB | 3P&N | 800 | 630 | 630 | Cable Ladder (Internal) - Touching | EC
MSB-N3-01/01 | UPS-N3A | STC-N3 | 3 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | ACB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N3-02/01 | UPS-N3B | STC-N3 | 3 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | ACB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
STC-N3-01 | STC-N3 | PDU-N3-1 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N3-02 | STC-N3 | PDU-N3-2 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N3-03 | STC-N3 | PDU-N3-3 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N3-04 | STC-N3 | PDU-N3-4 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N3-05 | STC-N3 | PDU-N3-5 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N3-06 | STC-N3 | PDU-N3-6 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N3-07 | STC-N3 | PDU-N3-7 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N3-08 | STC-N3 | PDU-N3-8 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
PDU-N3-1-1 | PDU-N3-1 | RB-GS1.MDF2-02-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-1-2 | PDU-N3-1 | RB-GS1.MDF1-01.1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-1-3 | PDU-N3-1 | RB-MDFC-01B-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-1-4 | PDU-N3-1 | RB-MDFD-02F-1A | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-2-1 | PDU-N3-2 | RB-MPOE1-03-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-2-2 | PDU-N3-2 | RB-MPOE1-02-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-2-3 | PDU-N3-2 | RB-GS2.MDF2-01-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-2-4 | PDU-N3-2 | RB-MDFA-02F-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-2-5 | PDU-N3-2 | RB-MDFA-01B-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-3-1 | PDU-N3-3 | RB-MDFB-01F-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-3-2 | PDU-N3-3 | RB-BDF1-02-4B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-3-3 | PDU-N3-3 | RB-MDFB-02B-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-3-4 | PDU-N3-3 | RB-MDFD-02B-1B | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-4-1 | PDU-N3-4 | RB-MPOE2-02-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-4-2 | PDU-N3-4 | RB-MDFA-02F-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-4-3 | PDU-N3-4 | RB-MDFA-02B-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-4-4 | PDU-N3-4 | RB-MDFB-01B-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-5-1 | PDU-N3-5 | RB-BDF1-03-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-5-2 | PDU-N3-5 | RB-MDFC-01F-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-5-3 | PDU-N3-5 | RB-MDFB-01F-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-5-4 | PDU-N3-5 | RB-MDFC-01F-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-6-1 | PDU-N3-6 | RB-MPOE2-02-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-6-2 | PDU-N3-6 | RB-BDF1-03-4A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-6-3 | PDU-N3-6 | RB-BDF1-02-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-6-4 | PDU-N3-6 | RB-MDFC-02B-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-7-1 | PDU-N3-7 | RB-BDF2-02-3A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-7-2 | PDU-N3-7 | RB-BDF2-03-4A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-7-3 | PDU-N3-7 | RB-MDFD-02B-2A | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-7-4 | PDU-N3-7 | RB-MDFD-01F-2B | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-8-1 | PDU-N3-8 | RB-BDF2-02-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-8-2 | PDU-N3-8 | RB-BDF2-03-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-8-3 | PDU-N3-8 | DB-NSR1-UPS-B | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N3-8-5 | PDU-N3-8 | DB-AD-UPS-2 | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N3-8-6 | PDU-N3-8 | DB-ESRA-UPS-B | 1 x 1 x 4c | 70 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N3-8-7 | PDU-N3-8 | DB-ESRB-UPS-B | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N3-8-8 | PDU-N3-8 | DB-HMDB-UPS-A | 1 x 1 x 4c | 50 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N3-01 | HMD-N3 | HMD-MDFB-N3 | 1 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 120 | MCCB | 3P&N | 400 | 400 | 400 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
HMD-N3-02 | HMD-N3 | HMD-MDFC-N2 | 1 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 120 | MCCB | 3P&N | 400 | 400 | 400 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
HMD-N3-03 | HMD-N3 | MPOE2.AHU.01 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N3-04 | HMD-N3 | BDF2.AHU.02 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N3-05 | HMD-N3 | BDF2.AHU.01 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N3-06 | HMD-N3 | ERN1.AHU.02 | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N3-07 | HMD-N3 | ERN1.AHU.04 | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N3-08 | HMD-N3 | ESRD AHU 01 (TEMPORARY SUPPLY) | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 250 | 160 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N2-01 | HMD-MDFC-N2 | MDF C SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N2-02 | HMD-MDFC-N2 | MDF C RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N2-04 | HMD-MDFC-N2 | MDF C AHU CP | 1 x 1 x 2c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N2-05 | HMD-MDFC-N2 | ECH PUMP MDF C AHU2. ECH | 1 x 1 x 2c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 16 | 16 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N2-06 | HMD-MDFC-N2 | MDFC.RIOA.ICPNL | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 25 | 25 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N2-07 | HMD-MDFC-N2 | MDF D SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N2-08 | HMD-MDFC-N2 | MDF D RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N3-01 | HMD-MDFD-N3 | MDF D SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N3-02 | HMD-MDFD-N3 | MDF D RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N3-04 | HMD-MDFD-N3 | MDF D AHU CP | 1 x 1 x 2c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N3-05 | HMD-MDFD-N3 | ECH PUMP MDF D AHU1. ECH | 1 x 1 x 2c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 16 | 16 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N3-06 | HMD-MDFD-N3 | MDFD.RIOA.ICPNL | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 25 | 25 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N3-07 | HMD-MDFD-N3 | MDF C SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N3-08 | HMD-MDFD-N3 | MDF C RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
PTX-N4-01 | PTX-N4-01 | MSB-N4 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
PTX-N4-02 | PTX-N4-02 | MSB-N4 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
EG-N4-01 | EG-N4 | MSB-N4 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
MSB-N4-01 | MSB-N4 | UPS-N4A | 3 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | MCCB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N4-02 | MSB-N4 | UPS-N4B | 3 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | MCCB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N4-03 | MSB-N4 | STC-N4 | 6 x 3 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 500 | MCCB | 3P | 4000 | 4000 | 3600 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N4-04 | MSB-N4 | HMD-N4 | 3 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 240 | MCCB | 3P&N | 1250 | 1250 | 1250 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
MSB-N4-05 | MSB-N4 | L-R-2R/N4 | 2 x 4 x 1c | 240 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 240 | MCCB | 3P&N | 1000 | 1000 | 1000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N4-06 | MSB-N4 | SPRINKLER MCCP ADMIN | 3 x 1 x 4c | 150 | Enhanced fire resistant, insulated & sheathed - FP 600S | 1 | Separate | 240 | MCCB | 3P&N | 800 | 630 | 630 | Cable Ladder (Internal) - Touching | EC
MSB-N4-01/01 | UPS-N4A | STC-N4 | 3 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | ACB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N4-02/01 | UPS-N4B | STC-N4 | 3 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | ACB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
STC-N4-01 | STC-N4 | PDU-N4-1 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N4-02 | STC-N4 | PDU-N4-2 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N4-03 | STC-N4 | PDU-N4-3 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N4-04 | STC-N4 | PDU-N4-4 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N4-05 | STC-N4 | PDU-N4-5 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N4-06 | STC-N4 | PDU-N4-6 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N4-07 | STC-N4 | PDU-N4-7 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N4-08 | STC-N4 | PDU-N4-8 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
PDU-N3-8-9 | PDU-N3-8 | ADM.VENT.EX.FAN7 | 1 x 1 x 4c | 50 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 40 | Cable Ladder (Internal) - Touching | EC
PDU-N4-1-1 | PDU-N4-1 | RB-MDFA-01F-1A | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-1-2 | PDU-N4-1 | RB-GS2.MDF2-01-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-1-3 | PDU-N4-1 | RB-MDFA-02B-1B | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-1-4 | PDU-N4-1 | RB-MDFD-01F-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-2-1 | PDU-N4-2 | RB-MDFA-01B-2A | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-2-2 | PDU-N4-2 | RB-MPOE1-03-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-2-3 | PDU-N4-2 | RB-MPOE2-03-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-2-4 | PDU-N4-2 | RB-MPOE2-03-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-2-5 | PDU-N4-2 | RB-MDFA-01F-2B | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-3-1 | PDU-N4-3 | RB-MDFB-02B-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-3-2 | PDU-N4-3 | RB-GS1.MDF2-02-1 | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-3-3 | PDU-N4-3 | RB-BDF1-02-3 | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-3-4 | PDU-N4-3 | RB-MDFB-02B-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-4-1 | PDU-N4-4 | RB-BDF2-03-3A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-4-2 | PDU-N4-4 | RB-MDFC-02F-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-4-3 | PDU-N4-4 | RB-BDF1-03-3B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-4-4 | PDU-N4-4 | RB-MDFB-01F-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-5-1 | PDU-N4-5 | RB-MDFB-02F-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-5-2 | PDU-N4-5 | RB-MPOE1-02-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-5-3 | PDU-N4-5 | RB-BDF1-02-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-5-4 | PDU-N4-5 | RB-MDFC-02F-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-5-5 | PDU-N4-5 | RB-MDFC-01B-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-6-1 | PDU-N4-6 | RB-MDFC-02B-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-6-2 | PDU-N4-6 | RB-BDF1-03-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-6-3 | PDU-N4-6 | RB-BDF2-03-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-6-4 | PDU-N4-6 | RB-MDFD-02B-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-7-1 | PDU-N4-7 | RB-MDFD-01F-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-7-2 | PDU-N4-7 | RB-GS1.MDF1-01.1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-7-3 | PDU-N4-7 | RB-BDF2-02-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-7-4 | PDU-N4-7 | RB-BDF2-02-4B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-8-1 | PDU-N4-8 | RB-MDFD-01B-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-8-2 | PDU-N4-8 | DB-NSR2-UPS-B | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N4-8-3 | PDU-N4-8 | DB-HMDN2-UPS | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N4-8-4 | PDU-N4-8 | DB-AD-UPS-1 | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N4-8-5 | PDU-N4-8 | DB-ESRC-UPS-B | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N4-8-6 | PDU-N4-8 | DB-ESRD-UPS-B | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N4-8-7 | PDU-N4-8 | DB-HMDD-UPS-A | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
HMD-N4-01 | HMD-N4 | HMD-MDFB-N4 | 1 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 120 | MCCB | 3P&N | 400 | 400 | 400 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
HMD-N4-02 | HMD-N4 | HMD-MDFD-N4 | 1 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 120 | MCCB | 3P&N | 400 | 400 | 400 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
HMD-N4-03 | HMD-N4 | MPOE2.AHU.02 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 50 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N4-04 | HMD-N4 | BDF2.AHU.03 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 50 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N4-05 | HMD-N4 | BDF2.AHU.02 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 50 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N4-06 | HMD-N4 | ERN2.AHU.02 | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N4-07 | HMD-N4 | ERN2.AHU.04 | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N4-08 | HMD-N4 | ESRC AHU-01 (TEMPORARY SUPPLY) | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 250 | 160 | 63 | Cable Ladder (Internal) - Touching | EC
HMD-MDFC-N1-01 | HMD-MDFC-N1 | MDF C SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N1-02 | HMD-MDFC-N1 | MDF C RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N1-04 | HMD-MDFC-N1 | MDF C AHU CP | 1 x 1 x 2c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N1-05 | HMD-MDFC-N1 | ECH PUMP MDF C AHU1. ECH | 1 x 1 x 2c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 16 | 16 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N1-06 | HMD-MDFC-N1 | MDFC.RIOB.ICPNL | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 25 | 25 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N1-07 | HMD-MDFC-N1 | MDF D SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N1-08 | HMD-MDFC-N1 | MDF D RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N4-01 | HMD-MDFD-N4 | MDF D SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N4-02 | HMD-MDFD-N4 | MDF D RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N4-04 | HMD-MDFD-N4 | MDF D AHU CP | 1 x 1 x 2c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N4-05 | HMD-MDFD-N4 | ECH PUMP MDF D AHU2. ECH | 1 x 1 x 2c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 16 | 16 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N4-06 | HMD-MDFD-N4 | MDFB.RIOA.ICPNL | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 25 | 25 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N4-07 | HMD-MDFD-N4 | MDF C SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N4-08 | HMD-MDFD-N4 | MDF C RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
LBSB-01-01 | LBSB-01 | MSB-N1 | 5000A Rated Bus Bar | Copper | 4 Pole Busbar Epoxy sandwich type | 1 | Case | - | ACB | 4P | 5000 | 5000 | 5000 | Independent Support | HPB/EC
LBSB-01-01 | LBSB-01 | STC-N1 | 5000A Rated Bus Bar | Copper | 4 Pole Busbar Epoxy sandwich type | 1 | Case | - | ACB | 4P | 4000 | 4000 | 4000 | Independent Support | HPB/EC
LBSB-01-01 | LBSB-01 | MSB-N3 | 5000A Rated Bus Bar | Copper | 4 Pole Busbar Epoxy sandwich type | 1 | Case | - | ACB | 4P | 5000 | 5000 | 5000 | Independent Support | HPB/EC
LBSB-01-01 | LBSB-01 | STC-N3 | 5000A Rated Bus Bar | Copper | 4 Pole Busbar Epoxy sandwich type | 1 | Case | - | ACB | 4P | 4000 | 4000 | 4000 | Independent Support | HPB/EC
LBSB-01-01 | LBSB-01 | MSB-N2 | 5000A Rated Bus Bar | Copper | 4 Pole Busbar Epoxy sandwich type | 1 | Case | - | ACB | 4P | 5000 | 5000 | 5000 | Independent Support | HPB/EC
LBSB-01-01 | LBSB-01 | STC-N2 | 5000A Rated Bus Bar | Copper | 4 Pole Busbar Epoxy sandwich type | 1 | Case | - | ACB | 4P | 4000 | 4000 | 4000 | Independent Support | HPB/EC
LBSB-01-01 | LBSB-01 | MSB-N4 | 5000A Rated Bus Bar | Copper | 4 Pole Busbar Epoxy sandwich type | 1 | Case | - | ACB | 4P | 5000 | 5000 | 5000 | Independent Support | HPB/EC
LBSB-01-01 | LBSB-01 | STC-N4 | 5000A Rated Bus Bar | Copper | 4 Pole Busbar Epoxy sandwich type | 1 | Case | - | ACB | 4P | 4000 | 4000 | 4000 | Independent Support | HPB/EC
LBSB-01-02 | LBSB-01 | MGCP-01 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
LBSB-01-03 | LBSB-01 | LOAD BANK-01 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC

## Cable_Schedule_ODN6
Schedule Name |  |  |  | Client | [6 empty] | Status
LV CABLES - ODN6 NETWORK CORE SCHEDULE |  |  |  | Cassin Network ApS | [6 empty] | ISSUE FOR ADDENDUM 1
Schedule Number
ODN56-E-SCH-0003
Project Name
Revision | Date |  |  | ODN56 Data Centre | [6 empty] | Prepared | Checked | Verified
1 | 2022-02-02 | [9 empty] | BP | JPr | JP
Notes: LVSV = Low Voltage Switchgear Vendor, EC = Electrical Contractor MVSV = Medium Voltage Switchgear Vendor, GV = Generator Vendor, HPB = High Power Bar Vendor Multicore Spacing (1 x OD), Single Core Quad./Trefoil (2 x OD)
LV CABLES - ODN6 NETWORK CORE SCHEDULE
Cable Information
Cable ID | Cable Routes |  | Cable Configuration | Cable Size (mm²) | Cable Type | No of CPCs | CPC Type | CPC Size (mm²) | Protective Device |  |  |  |  | Installation Method | Supplied and Installed By
| From | To | [6 empty] | Type | Poles | Frame Rating (A) | Device Rating (A) | Overload setting (A)
PTX-N1-01 | PTX-N1-01 | MSB-N1 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
PTX-N1-02 | PTX-N1-02 | MSB-N1 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
EG-N1-01 | EG-N1 | MSB-N1 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
MSB-N1-01 | MSB-N1 | UPS-N1A | 3 x 3 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | MCCB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N1-02 | MSB-N1 | UPS-N1B | 3 x 3 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | MCCB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N1-03 | MSB-N1 | STC-N1 | 6 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 500 | MCCB | 3P | 4000 | 4000 | 3600 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N1-04 | MSB-N1 | HMD-N1 | 3 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 240 | MCCB | 3P&N | 1250 | 1250 | 1250 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
MSB-N1-05 | MSB-N1 | L-R-1R/N1 | 3 x 4 x 1c | 240 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 240 | MCCB | 3P&N | 1000 | 1000 | 1000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N1-01/01 | UPS-N1A | STC-N1 | 3 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | ACB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N1-02/01 | UPS-N1B | STC-N1 | 3 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | ACB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
STC-N1-01 | STC-N1 | PDU-N1-1 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N1-02 | STC-N1 | PDU-N1-2 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N1-03 | STC-N1 | PDU-N1-3 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N1-04 | STC-N1 | PDU-N1-4 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N1-05 | STC-N1 | PDU-N1-5 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N1-06 | STC-N1 | PDU-N1-6 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N1-07 | STC-N1 | PDU-N1-7 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N1-08 | STC-N1 | PDU-N1-8 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
PDU-N1-1-1 | PDU-N1-1 | RB-GS1.MDF2-01-01A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-1-2 | PDU-N1-1 | RB-MPOE1-02-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-1-3 | PDU-N1-1 | RB-MDFA-02F-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-1-4 | PDU-N1-1 | RB-MDFB-02F-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-2-1 | PDU-N1-2 | RB-MPOE2-03-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-2-2 | PDU-N1-2 | RB-MPOE2-03-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-2-3 | PDU-N1-2 | RB-MDFD-02B-1A | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-2-4 | PDU-N1-2 | RB-MDFA-02F-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-3-1 | PDU-N1-3 | RB-MPOE1-03-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-3-2 | PDU-N1-3 | RB-BDF1-02-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-3-3 | PDU-N1-3 | RB-BDF1-03-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-3-4 | PDU-N1-3 | RB-MDFA-01B-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-3-5 | PDU-N1-3 | RB-MDFB-01B-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-4-1 | PDU-N1-4 | RB-GS2.MDF2-02-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-4-2 | PDU-N1-4 | RB-GS2.MDF1-01-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-4-3 | PDU-N1-4 | RB-BDF1-03-3A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-4-4 | PDU-N1-4 | RB-MDFB-01F-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-4-5 | PDU-N1-4 | RB-MDFC-01F-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-5-1 | PDU-N1-5 | RB-BDF1-02-4A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-5-2 | PDU-N1-5 | RB-BDF2-03-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-5-3 | PDU-N1-5 | RB-MDFA-02B-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-5-4 | PDU-N1-5 | RB-MDFC-01B-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-6-1 | PDU-N1-6 | RB-MDFB-01B-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-6-2 | PDU-N1-6 | RB-MDFC-01B-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-6-3 | PDU-N1-6 | RB-MDFD-02F-2A | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-6-4 | PDU-N1-6 | RB-MDFC-02F-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-7-1 | PDU-N1-7 | RB-BDF2-02-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-7-2 | PDU-N1-7 | RB-BDF2-02-3B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-7-3 | PDU-N1-7 | RB-BDF2-03-3B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-7-4 | PDU-N1-7 | RB-MDFD-01B-1B | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-8-1 | PDU-N1-8 | DB-ESRA-UPS-A | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N1-8-2 | PDU-N1-8 | DB-ESRB-UPS-A | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N1-8-3 | PDU-N1-8 | DB-HMDA-UPS-A | 1 x 1 x 4c | 50 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N1-8-4 | PDU-N1-8 | DB-IDF-UPS-A | 1 x 1 x 4c | 185 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-8-5 | PDU-N1-8 | DB-HMDN1-UPS | 1 x 1 x 4c | 50 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
PDU-N1-8-6 | PDU-N1-8 | RB-MDFD-02F-1B | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N1-8-7 | PDU-N1-8 | DB-NSR1-UPS-A | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
HMD-N1-01 | HMD-N1 | HMD-MDFA-N1 | 1 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 120 | MCCB | 3P&N | 400 | 400 | 400 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
HMD-N1-02 | HMD-N1 | HMD-MDFC-N1 | 1 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 120 | MCCB | 3P&N | 400 | 400 | 400 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
HMD-N1-03 | HMD-N1 | MPOE1.AHU.01 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N1-04 | HMD-N1 | BDF1.AHU.02 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N1-05 | HMD-N1 | BDF1.AHU.01 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N1-06 | HMD-N1 | ERN1.AHU.01 | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N1-07 | HMD-N1 | ERN1.AHU.03 | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N1-08 | HMD-N1 | DB-HMDN1-LP | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 250 | 250 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N2-01 | HMD-MDFA-N2 | MDF A SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N2-02 | HMD-MDFA-N2 | MDF A RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N2-04 | HMD-MDFA-N2 | MDF A AHU CP | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N2-05 | HMD-MDFA-N2 | ECH PUMP MDF A AHU1. ECH | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 16 | 16 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N2-06 | HMD-MDFA-N2 | MDFA.RIOB.ICPNL | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 25 | 25 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N2-07 | HMD-MDFA-N2 | MDF B SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N2-08 | HMD-MDFA-N2 | MDF B RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N3-01 | HMD-MDFB-N3 | MDF B SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N3-02 | HMD-MDFB-N3 | MDF B RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N3-04 | HMD-MDFB-N3 | MDF B AHU CP | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N3-05 | HMD-MDFB-N3 | ECH PUMP MDF B AHU2. ECH | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 16 | 16 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N3-06 | HMD-MDFB-N2 | MDFA.RIOB.ICPNL | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 25 | 25 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N3-07 | HMD-MDFB-N3 | MDF A SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N3-08 | HMD-MDFB-N3 | MDF A RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
PTX-N2-01 | PTX-N2-01 | MSB-N2 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
PTX-N2-02 | PTX-N2-02 | MSB-N2 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
EG-N2-01 | EG-N2 | MSB-N2 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
MSB-N2-01 | MSB-N2 | UPS-N2A | 3 x 3 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | MCCB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N2-02 | MSB-N2 | UPS-N2B | 3 x 3 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | MCCB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N2-03 | MSB-N2 | STC-N2 | 6 x 3 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 500 | MCCB | 3P | 4000 | 4000 | 3600 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N2-04 | MSB-N2 | HMD-N2 | 3 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 240 | MCCB | 3P&N | 1250 | 1250 | 1250 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
MSB-N2-05 | MSB-N2 | L-R-2R/N2 | 3 x 4 x 1c | 240 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 240 | MCCB | 3P&N | 1000 | 1000 | 1000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N2-01/01 | UPS-N2A | STC-N2 | 3 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | ACB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N2-02/01 | UPS-N2B | STC-N2 | 3 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | ACB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
STC-N2-01 | STC-N2 | PDU-N2-1 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N2-02 | STC-N2 | PDU-N2-2 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N2-03 | STC-N2 | PDU-N2-3 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N2-04 | STC-N2 | PDU-N2-4 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N2-05 | STC-N2 | PDU-N2-5 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N2-06 | STC-N2 | PDU-N2-6 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N2-07 | STC-N2 | PDU-N2-7 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N2-08 | STC-N2 | PDU-N2-8 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
PDU-N2-1-1 | PDU-N2-1 | RB-GS1.MDF2-01-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-1-2 | PDU-N2-1 | RB-MPOE1-03-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-1-3 | PDU-N2-1 | RB-GS2.MDF2-02-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-1-4 | PDU-N2-1 | RB-BDF1-03-4B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-1-5 | PDU-N2-1 | RB-MDFD-01B-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-2-1 | PDU-N2-2 | RB-BDF2-02-4A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-2-2 | PDU-N2-2 | RB-MDFA-01F-2A | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-2-3 | PDU-N2-2 | RB-MPOE1-02-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-2-4 | PDU-N2-2 | RB-MPOE2-02-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-2-5 | PDU-N2-2 | RB-MDFB-01B-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-3-1 | PDU-N2-3 | RB-MDFB-02F-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-3-2 | PDU-N2-3 | RB-MDFB-02B-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-3-3 | PDU-N2-3 | RB-BDF2-02-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-3-4 | PDU-N2-3 | RB-MDFA-01F-1B | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-4-1 | PDU-N2-4 | RB-BDF2-03-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-4-2 | PDU-N2-4 | RB-MDFA-02B-2B | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-4-3 | PDU-N2-4 | RB-MDFC-01F-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-4-4 | PDU-N2-4 | RB-MDFC-02B-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-5-1 | PDU-N2-5 | RB-MPOE2-02-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-5-2 | PDU-N2-5 | RB-BDF1-02-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-5-3 | PDU-N2-5 | RB-BDF1-03-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-5-4 | PDU-N2-5 | RB-MDFB-02F-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-6-1 | PDU-N2-6 | RB-MDFA-01B-1A | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-6-2 | PDU-N2-6 | RB-MDFC-02F-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-6-3 | PDU-N2-6 | RB-MDFC-02B-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-7-1 | PDU-N2-7 | RB-BDF1-02-3A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-7-2 | PDU-N2-7 | RB-MDFD-01F-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-7-3 | PDU-N2-7 | RB-GS2.MDF1-01-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-7-4 | PDU-N2-7 | RB-BDF2-03-4B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-8-1 | PDU-N2-8 | RB-MDFD-01B-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-8-2 | PDU-N2-8 | DB-ESRC-UPS-A | 1 x 1 x 4c | 50 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N2-8-3 | PDU-N2-8 | DB-ESRD-UPS-A | 1 x 1 x 4c | 50 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N2-8-4 | PDU-N2-8 | DB-HMDC-UPS-A | 1 x 1 x 4c | 50 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
PDU-N2-8-5 | PDU-N2-8 | DB-IDF-UPS-B | 1 x 1 x 4c | 120 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-8-6 | PDU-N2-8 | ADM.VENT.EX.FAN6 | 1 x 1 x 4c | 50 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 40 | Cable Ladder (Internal) - Touching | EC
PDU-N2-8-7 | PDU-N2-8 | RB-MDFD-02F-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N2-8-8 | PDU-N2-8 | DB-NSR2-UPS-B | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 250 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
HMD-N2-01 | HMD-N2 | HMD-MDFA-N2 | 1 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 120 | MCCB | 3P&N | 400 | 400 | 400 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
HMD-N2-02 | HMD-N2 | HMD-MDFC-N2 | 1 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 120 | MCCB | 3P&N | 400 | 400 | 400 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
HMD-N2-03 | HMD-N2 | MPOE1.AHU.02 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N2-04 | HMD-N2 | BDF1 AHU.03 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N2-05 | HMD-N2 | BDF1.AHU.02 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N2-06 | HMD-N2 | ERN2.AHU.01 | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N2-07 | HMD-N2 | ERN2.AHU.03 | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N2-08 | HMD-N2 | DB-HMDN2-LP | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 250 | 250 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N1-01 | HMD-MDFA-N1 | MDF B SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N1-02 | HMD-MDFA-N1 | MDF B RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N1-04 | HMD-MDFA-N1 | MDF B AHU CP | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N1-05 | HMD-MDFA-N1 | ECH PUMP MDF B AHU1. ECH | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 16 | 16 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N1-06 | HMD-MDFA-N1 | MDFA.RIOA.ICPNL | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 40 | 25 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N1-07 | HMD-MDFA-N1 | MDF B SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 25 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFA-N1-08 | HMD-MDFA-N1 | MDF B RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N4-01 | HMD-MDFB-N4 | MDF B SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N4-02 | HMD-MDFB-N4 | MDF B RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N4-04 | HMD-MDFB-N4 | MDF B AHU CP | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N4-05 | HMD-MDFB-N4 | ECH PUMP MDF B AHU1. ECH | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 16 | 16 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N4-06 | HMD-MDFB-N4 | MDFB.RIOA.ICPNL | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 40 | 25 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N4-07 | HMD-MDFB-N4 | MDF B SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 25 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFB-N4-08 | HMD-MDFB-N4 | MDF B RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
PTX-N3-01 | PTX-N3-01 | MSB-N3 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
PTX-N3-02 | PTX-N3-02 | MSB-N3 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
EG-N3-01 | EG-N3 | MSB-N3 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
MSB-N3-01 | MSB-N3 | UPS-N3A | 3 x 3 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | MCCB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N3-02 | MSB-N3 | UPS-N3B | 3 x 3 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | MCCB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N3-03 | MSB-N3 | STC-N3 | 6 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 500 | MCCB | 3P | 4000 | 4000 | 3600 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N3-04 | MSB-N3 | HMD-N3 | 3 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 240 | MCCB | 3P&N | 1250 | 1250 | 1250 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
MSB-N3-05 | MSB-N3 | L-R-1R/N3 | 2 x 4 x 1c | 240 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 240 | MCCB | 3P&N | 1000 | 1000 | 1000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N3-06 | MSB-N3 | SPRINKLER MCCP ADMIN | 3 x 1 x 4c | 150 | Enhanced fire resistant, insulated & sheathed - FP 600S | 1 | Separate | 240 | MCCB | 3P&N | 800 | 630 | 630 | Cable Ladder (Internal) - Touching | EC
MSB-N3-01/01 | UPS-N3A | STC-N3 | 3 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | ACB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N3-02/01 | UPS-N3B | STC-N3 | 3 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | ACB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
STC-N3-01 | STC-N3 | PDU-N3-1 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N3-02 | STC-N3 | PDU-N3-2 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N3-03 | STC-N3 | PDU-N3-3 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N3-04 | STC-N3 | PDU-N3-4 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N3-05 | STC-N3 | PDU-N3-5 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N3-06 | STC-N3 | PDU-N3-6 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N3-07 | STC-N3 | PDU-N3-7 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N3-08 | STC-N3 | PDU-N3-8 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
PDU-N3-1-1 | PDU-N3-1 | RB-GS1.MDF2-02-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-1-2 | PDU-N3-1 | RB-GS1.MDF1-01.1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-1-3 | PDU-N3-1 | RB-MDFC-01B-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-1-4 | PDU-N3-1 | RB-MDFD-02F-1A | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-2-1 | PDU-N3-2 | RB-MPOE1-03-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-2-2 | PDU-N3-2 | RB-MPOE1-02-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-2-3 | PDU-N3-2 | RB-GS2.MDF2-01-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-2-4 | PDU-N3-2 | RB-MDFA-02F-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-2-5 | PDU-N3-2 | RB-MDFA-01B-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-3-1 | PDU-N3-3 | RB-MDFB-01F-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-3-2 | PDU-N3-3 | RB-BDF1-02-4B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-3-3 | PDU-N3-3 | RB-MDFB-02B-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-3-4 | PDU-N3-3 | RB-MDFD-02B-1B | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-4-1 | PDU-N3-4 | RB-MPOE2-02-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-4-2 | PDU-N3-4 | RB-MDFA-02F-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-4-3 | PDU-N3-4 | RB-MDFA-02B-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-4-4 | PDU-N3-4 | RB-MDFB-01B-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-5-1 | PDU-N3-5 | RB-BDF1-03-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-5-2 | PDU-N3-5 | RB-MDFC-01F-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-5-3 | PDU-N3-5 | RB-MDFB-01F-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-5-4 | PDU-N3-5 | RB-MDFC-01F-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-6-1 | PDU-N3-6 | RB-MPOE2-02-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-6-2 | PDU-N3-6 | RB-BDF1-03-4A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-6-3 | PDU-N3-6 | RB-BDF1-02-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-6-4 | PDU-N3-6 | RB-MDFC-02B-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-7-1 | PDU-N3-7 | RB-BDF2-02-3A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-7-2 | PDU-N3-7 | RB-BDF2-03-4A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-7-3 | PDU-N3-7 | RB-MDFD-02B-2A | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-7-4 | PDU-N3-7 | RB-MDFD-01F-2B | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-8-1 | PDU-N3-8 | RB-BDF2-02-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-8-2 | PDU-N3-8 | RB-BDF2-03-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N3-8-3 | PDU-N3-8 | DB-NSR1-UPS-B | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N3-8-5 | PDU-N3-8 | DB-AD-UPS-2 | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N3-8-6 | PDU-N3-8 | DB-ESRA-UPS-B | 1 x 1 x 4c | 70 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N3-8-7 | PDU-N3-8 | DB-ESRB-UPS-B | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N3-8-8 | PDU-N3-8 | DB-HMDB-UPS-A | 1 x 1 x 4c | 50 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N3-01 | HMD-N3 | HMD-MDFB-N3 | 1 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 120 | MCCB | 3P&N | 400 | 400 | 400 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
HMD-N3-02 | HMD-N3 | HMD-MDFC-N2 | 1 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 120 | MCCB | 3P&N | 400 | 400 | 400 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
HMD-N3-03 | HMD-N3 | MPOE2.AHU.01 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N3-04 | HMD-N3 | BDF2.AHU.02 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N3-05 | HMD-N3 | BDF2.AHU.01 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N3-06 | HMD-N3 | ERN1.AHU.02 | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N3-07 | HMD-N3 | ERN1.AHU.04 | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N3-08 | HMD-N3 | ESRA AHU 01 (TEMPORARY SUPPLY) | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 250 | 160 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N2-01 | HMD-MDFC-N2 | MDF C SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N2-02 | HMD-MDFC-N2 | MDF C RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N2-04 | HMD-MDFC-N2 | MDF C AHU CP | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N2-05 | HMD-MDFC-N2 | ECH PUMP MDF C AHU2. ECH | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 16 | 16 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N2-06 | HMD-MDFC-N2 | MDFC.RIOA.ICPNL | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 25 | 25 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N2-07 | HMD-MDFC-N2 | MDF D SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N2-08 | HMD-MDFC-N2 | MDF D RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N3-01 | HMD-MDFD-N3 | MDF D SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N3-02 | HMD-MDFD-N3 | MDF D RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N3-04 | HMD-MDFD-N3 | MDF D AHU CP | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N3-05 | HMD-MDFD-N3 | ECH PUMP MDF D AHU1. ECH | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 16 | 16 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N3-06 | HMD-MDFD-N3 | MDFD.RIOA.ICPNL | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 25 | 25 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N3-07 | HMD-MDFD-N3 | MDF C SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N3-08 | HMD-MDFD-N3 | MDF C RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
PTX-N4-01 | PTX-N4-01 | MSB-N4 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
PTX-N4-02 | PTX-N4-02 | MSB-N4 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
EG-N4-01 | EG-N4 | MSB-N4 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
MSB-N4-01 | MSB-N4 | UPS-N4A | 3 x 3 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | MCCB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N4-02 | MSB-N4 | UPS-N4B | 3 x 3 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | MCCB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N4-03 | MSB-N4 | STC-N4 | 6 x 3 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 500 | MCCB | 3P | 4000 | 4000 | 3600 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N4-04 | MSB-N4 | HMD-N4 | 3 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 240 | MCCB | 3P&N | 1250 | 1250 | 1250 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
MSB-N4-05 | MSB-N4 | L-R-2R/N4 | 2 x 4 x 1c | 240 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 240 | MCCB | 3P&N | 1000 | 1000 | 1000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N4-06 | MSB-N4 | SPRINKLER MCCP ADMIN | 3 x 1 x 4c | 150 | Enhanced fire resistant, insulated & sheathed - FP 600S | 1 | Separate | 240 | MCCB | 3P&N | 800 | 630 | 630 | Cable Ladder (Internal) - Touching | EC
MSB-N4-01/01 | UPS-N4A | STC-N4 | 3 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | ACB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
MSB-N4-02/01 | UPS-N4B | STC-N4 | 3 x 4 x 1c | 400 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 400 | ACB | 3P | 2000 | 2000 | 2000 | Cable Ladder in Floor Void - Quad/Trefoil | LVSV
STC-N4-01 | STC-N4 | PDU-N4-1 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N4-02 | STC-N4 | PDU-N4-2 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N4-03 | STC-N4 | PDU-N4-3 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N4-04 | STC-N4 | PDU-N4-4 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N4-05 | STC-N4 | PDU-N4-5 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N4-06 | STC-N4 | PDU-N4-6 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N4-07 | STC-N4 | PDU-N4-7 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
STC-N4-08 | STC-N4 | PDU-N4-8 | 2 x 3 x 1c | 300 | Single-core Class 5 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 150 | MCCB | 3P | 800 | 800 | 640 | Cable Ladder (Internal) - Quad/Trefoil | LVSV
PDU-N3-8-9 | PDU-N3-8 | ADM.VENT.EX.FAN7 | 1 x 1 x 4c | 50 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 40 | Cable Ladder (Internal) - Touching | EC
PDU-N4-1-1 | PDU-N4-1 | RB-MDFA-01F-1A | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-1-2 | PDU-N4-1 | RB-GS2.MDF2-01-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-1-3 | PDU-N4-1 | RB-MDFA-02B-1B | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-1-4 | PDU-N4-1 | RB-MDFD-01F-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-2-1 | PDU-N4-2 | RB-MDFA-01B-2A | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-2-2 | PDU-N4-2 | RB-MPOE1-03-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-2-3 | PDU-N4-2 | RB-MPOE2-03-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-2-4 | PDU-N4-2 | RB-MPOE2-03-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-2-5 | PDU-N4-2 | RB-MDFA-01F-2B | 1 x 1 x 4c | 185 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 95 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-3-1 | PDU-N4-3 | RB-MDFB-02B-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-3-2 | PDU-N4-3 | RB-GS1.MDF2-02-1 | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-3-3 | PDU-N4-3 | RB-BDF1-02-3 | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-3-4 | PDU-N4-3 | RB-MDFB-02B-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-4-1 | PDU-N4-4 | RB-BDF2-03-3A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-4-2 | PDU-N4-4 | RB-MDFC-02F-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-4-3 | PDU-N4-4 | RB-BDF1-03-3B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-4-4 | PDU-N4-4 | RB-MDFB-01F-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-5-1 | PDU-N4-5 | RB-MDFB-02F-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-5-2 | PDU-N4-5 | RB-MPOE1-02-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-5-3 | PDU-N4-5 | RB-BDF1-02-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-5-4 | PDU-N4-5 | RB-MDFC-02F-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-5-5 | PDU-N4-5 | RB-MDFC-01B-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-6-1 | PDU-N4-6 | RB-MDFC-02B-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-6-2 | PDU-N4-6 | RB-BDF1-03-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-6-3 | PDU-N4-6 | RB-BDF2-03-1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-6-4 | PDU-N4-6 | RB-MDFD-02B-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-7-1 | PDU-N4-7 | RB-MDFD-01F-2A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-7-2 | PDU-N4-7 | RB-GS1.MDF1-01.1B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-7-3 | PDU-N4-7 | RB-BDF2-02-2B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-7-4 | PDU-N4-7 | RB-BDF2-02-4B | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-8-1 | PDU-N4-8 | RB-MDFD-01B-1A | 1 x 1 x 4c | 120 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 50 | MCCB | 3P&N | 250 | 250 | 250 | Cable Ladder (Internal) - Touching | EC
PDU-N4-8-2 | PDU-N4-8 | DB-NSR2-UPS-B | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N4-8-3 | PDU-N4-8 | DB-HMDN2-UPS | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N4-8-4 | PDU-N4-8 | DB-AD-UPS-1 | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N4-8-5 | PDU-N4-8 | DB-ESRC-UPS-B | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N4-8-6 | PDU-N4-8 | DB-ESRD-UPS-B | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
PDU-N4-8-7 | PDU-N4-8 | DB-HMDD-UPS-A | 1 x 1 x 4c | 50 | Multicore Class 2 N2XH Cable, Enhanced FRNC-LSZH, KEMA Approved Cable | 1 | Separate | 35 | MCCB | 3P&N | 100 | 100 | 100 | Cable Ladder (Internal) - Touching | EC
HMD-N4-01 | HMD-N4 | HMD-MDFB-N4 | 1 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 120 | MCCB | 3P&N | 400 | 400 | 400 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
HMD-N4-02 | HMD-N4 | HMD-MDFD-N4 | 1 x 4 x 1c | 240 | Single-core Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 120 | MCCB | 3P&N | 400 | 400 | 400 | Cable Ladder (External/ Internal) - Quad/Trefoil | EC
HMD-N4-03 | HMD-N4 | MPOE2.AHU.02 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 50 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N4-04 | HMD-N4 | BDF2.AHU.03 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 50 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N4-05 | HMD-N4 | BDF2.AHU.02 | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 50 | MCCB | 3P&N | 160 | 160 | 160 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N4-06 | HMD-N4 | ERN2.AHU.02 | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N4-07 | HMD-N4 | ERN2.AHU.04 | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 100 | Cable Ladder (External/ Internal) - Touching | EC
HMD-N4-08 | HMD-N4 | ESRB AHU-01 (TEMPORARY SUPPLY) | 1 x 1 x 4c | 35 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 250 | 160 | 63 | Cable Ladder (Internal) - Touching | EC
HMD-MDFC-N1-01 | HMD-MDFC-N1 | MDF C SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N1-02 | HMD-MDFC-N1 | MDF C RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N1-04 | HMD-MDFC-N1 | MDF C AHU CP | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N1-05 | HMD-MDFC-N1 | ECH PUMP MDF C AHU1. ECH | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 16 | 16 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N1-06 | HMD-MDFC-N1 | MDFC.RIOB.ICPNL | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 25 | 25 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N1-07 | HMD-MDFC-N1 | MDF D SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N1-08 | HMD-MDFC-N1 | MDF D RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N4-01 | HMD-MDFD-N4 | MDF D SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N4-02 | HMD-MDFD-N4 | MDF D RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N4-04 | HMD-MDFD-N4 | MDF D AHU CP | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N4-05 | HMD-MDFD-N4 | ECH PUMP MDF D AHU2. ECH | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 16 | 16 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFC-N4-06 | HMD-MDFD-N4 | MDFB.RIOA.ICPNL | 1 x 1 x 3c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 1P&N | 160 | 25 | 25 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N4-07 | HMD-MDFD-N4 | MDF C SUPPLY FANS | 1 x 1 x 4c | 70 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 35 | MCCB | 3P&N | 160 | 100 | 63 | Cable Ladder (External/ Internal) - Touching | EC
HMD-MDFD-N4-08 | HMD-MDFD-N4 | MDF C RELIEF FANS | 1 x 1 x 4c | 6 | Multicore Thermosetting insulated & LSZH Sheathed Armoured Cable | 1 | Separate | 6 | MCCB | 3P&N | 160 | 40 | 32 | Cable Ladder (External/ Internal) - Touching | EC
LBSB-01-01 | LBSB-01 | MSB-N1 | 5000A Rated Bus Bar | Copper | 4 Pole Busbar Epoxy sandwich type | 1 | Case | - | ACB | 4P | 5000 | 5000 | 5000 | Independent Support | HPB/EC
LBSB-01-01 | LBSB-01 | STC-N1 | 5000A Rated Bus Bar | Copper | 4 Pole Busbar Epoxy sandwich type | 1 | Case | - | ACB | 4P | 4000 | 4000 | 4000 | Independent Support | HPB/EC
LBSB-01-01 | LBSB-01 | MSB-N3 | 5000A Rated Bus Bar | Copper | 4 Pole Busbar Epoxy sandwich type | 1 | Case | - | ACB | 4P | 5000 | 5000 | 5000 | Independent Support | HPB/EC
LBSB-01-01 | LBSB-01 | STC-N3 | 5000A Rated Bus Bar | Copper | 4 Pole Busbar Epoxy sandwich type | 1 | Case | - | ACB | 4P | 4000 | 4000 | 4000 | Independent Support | HPB/EC
LBSB-01-01 | LBSB-01 | MSB-N2 | 5000A Rated Bus Bar | Copper | 4 Pole Busbar Epoxy sandwich type | 1 | Case | - | ACB | 4P | 5000 | 5000 | 5000 | Independent Support | HPB/EC
LBSB-01-01 | LBSB-01 | STC-N2 | 5000A Rated Bus Bar | Copper | 4 Pole Busbar Epoxy sandwich type | 1 | Case | - | ACB | 4P | 4000 | 4000 | 4000 | Independent Support | HPB/EC
LBSB-01-01 | LBSB-01 | MSB-N4 | 5000A Rated Bus Bar | Copper | 4 Pole Busbar Epoxy sandwich type | 1 | Case | - | ACB | 4P | 5000 | 5000 | 5000 | Independent Support | HPB/EC
LBSB-01-01 | LBSB-01 | STC-N4 | 5000A Rated Bus Bar | Copper | 4 Pole Busbar Epoxy sandwich type | 1 | Case | - | ACB | 4P | 4000 | 4000 | 4000 | Independent Support | HPB/EC
LBSB-01-02 | LBSB-01 | MGCP-01 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC
LBSB-01-03 | LBSB-01 | LOAD BANK-01 | 10 x 4 x 1c | 500 | Single-core H07ZZ-F Cable, Double Rubber LSOH Insulated Flexible Cable, in accordance with DS EN 50525-3-21 | 2 | Separate | 500 | ACB | 4P | 5000 | 5000 | 5000 | Below Ground Cable Duct Installation & Cable Ladder in Floor Void - Quad/Trefoil | EC